## Sheet1
Art.Nr. | Bezeichnung deutsch | Bezeichnung englisch | Produktgruppe | Untergruppe | Typnr. | Bemess.- Spannung UL AC (V) | Bemess.- Spannung UL DC (V) | Bemess.- strom UL (A) | max. Belastbarkeit entsprechend UL 508 | Belastung bei 50 K | Belastung bei 60 K | SCCR (kA) | SCCR unprotected max. | Bedingung SCCR unprotected max. | SCCR protected max. | Bedingung SCCR protected max. | SCCR Text | geeignet für feeder circuits >250V nach UL 508A | geeignet für field-installed conductors | Art der UL Zulassung | UL file | UL category | UL category (Canada) | UL file 2 | UL category 2 | UL category 2 (Canada) | CSA file | CSA Class | Link Deutsch | Link Englisch
part no. | description German | description English | product group | sub group | type no. | rated voltage UL AC (V) | rated voltage UL DC (V) | rated current UL (A) | max. capacity acc. UL 508 | capacity at 50 K | capacity at 60 K | SCCR (kA) | SCCR unprotected max. | condition for SCCR unprotected max. | SCCR protected max. | condition for SCCR protected max. | SCCR text | suitable for feeder circuits >250V acc. UL 508A | suitable for field-installed conductors | kind of UL approval | UL file | UL category | UL category (Canada) | UL file 2 | UL category 2 | UL category 2 (Canada) | CSA file | CSA Class | link German | link English
01008 | Profilklemme | profile terminal | 07 | 30 | HH64.2 | 600 |  | 1400 |  |  |  | 35 | [5 empty] | No |  | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01008.html | www.woehner.com/en/products/01008.html
01025 | Abdeckprofil | busbar section cover | 06 | 27 | C025-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01025.html | www.woehner.com/en/products/01025.html
01026 | Halter für Abdeckprofil | mount for busbar section cover | 06 | 27 | C026-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01026.html | www.woehner.com/en/products/01026.html
01027 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 3x20x1 |  |  |  |  | 345 | 400 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01027.html | www.woehner.com/en/products/01027.html
01028 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 6x20x1 |  |  |  |  | 515 | 595 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01028.html | www.woehner.com/en/products/01028.html
01029 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 10x20x1 |  |  |  |  | 705 | 810 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01029.html | www.woehner.com/en/products/01029.html
01035 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 6x15,5x0,8 |  |  |  |  | 375 | 430 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01035.html | www.woehner.com/en/products/01035.html
01054 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 3x9x0,8 |  |  |  |  | 165 | 195 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01054.html | www.woehner.com/en/products/01054.html
01060 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 5x50x1 |  |  |  |  | 965 | 1110 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01060.html | www.woehner.com/en/products/01060.html
01061 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 10x80x1 |  |  |  |  | 1960 | 2260 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01061.html | www.woehner.com/en/products/01061.html
01063 | Lamellierte Kupferschiene, verzinnt, isoliert | flexible copper busbar, tinned, insulated | 06 | 81 | 6x20x1 |  |  |  |  | 515 | 595 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01063.html | www.woehner.com/en/products/01063.html
01064 | Lamellierte Kupferschiene, verzinnt, isoliert | flexible copper busbar, tinned, insulated | 06 | 81 | 10x20x1 |  |  |  |  | 705 | 810 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01064.html | www.woehner.com/en/products/01064.html
01068 | Univ.-Leiteranschluss-Klemme | universal conductor terminal | 07 | 18 | 524 | 600 |  | 255 |  |  |  | 18 | [7 empty] | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01068.html | www.woehner.com/en/products/01068.html
01069 | Spreizklemme | brace terminal | 07 | 30 | CPC50-L | 600 |  | 1200 |  |  |  | 25 | [5 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01069.html | www.woehner.com/en/products/01069.html
01070 | Spreizklemme | brace terminal | 07 | 30 | CPC63-L | 600 |  | 1400 |  |  |  | 25 | [5 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01070.html | www.woehner.com/en/products/01070.html
01071 | Spreizklemme | brace terminal | 07 | 30 | CPC100-L | 600 |  | 1800 |  |  |  | 35 | [5 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01071.html | www.woehner.com/en/products/01071.html
01075 | Lamellierte Kupferschiene, verzinnt, isoliert | flexible copper busbar, tinned, insulated | 06 | 81 | 5x24x1 |  |  |  |  | 535 | 615 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01075.html | www.woehner.com/en/products/01075.html
01076 | Lamellierte Kupferschiene, verzinnt, isoliert | flexible copper busbar, tinned, insulated | 06 | 81 | 10x24x1 |  |  |  |  | 800 | 925 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01076.html | www.woehner.com/en/products/01076.html
01089 | Lamellierte Kupferschiene, verzinnt, isoliert | flexible copper busbar, tinned, insulated | 06 | 81 | 4x15,5x0,8 |  |  |  |  | 295 | 340 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01084.html | www.woehner.com/en/products/01084.html
01090 | Lamellierte Kupferschiene, verzinnt, isoliert | flexible copper busbar, tinned, insulated | 06 | 81 | 6x15,5x0,8 |  |  |  |  | 375 | 430 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01089.html | www.woehner.com/en/products/01089.html
01091 | Lamellierte Kupferschiene, verzinnt, isoliert | flexible copper busbar, tinned, insulated | 06 | 81 | 10x15,5x0,8 |  |  |  |  | 510 | 590 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01090.html | www.woehner.com/en/products/01090.html
01095 | Lamellierte Kupferschiene, verzinnt, isoliert | flexible copper busbar, tinned, insulated | 06 | 81 | 5x32x1 |  |  |  |  | 670 | 775 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01091.html | www.woehner.com/en/products/01091.html
01096 | lamellierte Kupferschiene, verzinnt, isoliert | flexible copper busbar, tinned, insulated | 06 | 81 | 10x32x1 |  |  |  |  | 985 | 1135 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01095.html | www.woehner.com/en/products/01095.html
01097 | Lamellierte Kupferschiene, verzinnt, isoliert | flexible copper busbar, tinned, insulated | 06 | 81 | 5x40x1 |  |  | 805 |  | 805 | 925 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01096.html | www.woehner.com/en/products/01096.html
01099 | Lamellierte Kupferschiene, verzinnt, isoliert | flexible copper busbar, tinned, insulated | 06 | 81 | 10x40x1 |  |  |  |  | 1160 | 1340 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01097.html | www.woehner.com/en/products/01097.html
01112 | Lamellierte Kupferschiene, verzinnt, isoliert | flexible copper busbar, tinned, insulated | 06 | 81 | 5x50x1 |  |  |  |  | 965 | 1110 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01099.html | www.woehner.com/en/products/01099.html
01113 | Lamellierte Kupferschiene, verzinnt, isoliert | flexible copper busbar, tinned, insulated | 06 | 81 | 10x50x1 |  |  |  |  | 1375 | 1585 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01112.html | www.woehner.com/en/products/01112.html
01116 | Sammelschienenträger | busbar support | 06 | 03 | S635-L | 600 | [11 empty] | Yes |  | UL listed | E123577 | NMTR | [6 empty] | www.woehner.com/de/products/01113.html | www.woehner.com/en/products/01113.html
01123 | Lamellierte Kupferschiene, verzinnt, isoliert | flexible copper busbar, tinned, insulated | 06 | 81 | 10x63x1 |  |  |  |  | 1630 | 1875 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01116.html | www.woehner.com/en/products/01116.html
01131 | Endabdeckung | end cover | 06 | 27 | 511-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01123.html | www.woehner.com/en/products/01123.html
01132 | Sammelschienenträger | busbar support | 06 | 03 | S645-L | 600 | [11 empty] | Yes |  | UL listed | E123577 | NMTR | [6 empty] | www.woehner.com/de/products/01131.html | www.woehner.com/en/products/01131.html
01135 | Spreizklemme | brace terminal | 07 | 19 | 515-L | 600 |  | 285 |  |  |  | 18 | [5 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01132.html | www.woehner.com/en/products/01132.html
01136 | Haltegarnitur für Abdeckprofile, für 3-polige Sammelschienensysteme | set of holders for cover sections, for 3-pole busbar systems | 07 | 36 | TC60-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01135.html | www.woehner.com/en/products/01135.html
01137 | Haltegarnitur für Abdeckprofile, für 4-polige Sammelschienensysteme | set of holders for cover sections, for 4-pole busbar systems | 07 | 36 | TC60-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01136.html | www.woehner.com/en/products/01136.html
01140 | Sammelschiene 20 x 10 | busbar 20 x 10 | 06 | 83 | 20x10-L |  |  |  | 564 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01137.html | www.woehner.com/en/products/01137.html
01141 | Schienen-Längsverbindung 630 A | busbar connecting terminal 630 A | 07 | 33 | LV30-L |  |  | 756 |  |  |  | 25 | [5 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01140.html | www.woehner.com/en/products/01140.html
01145 | Schienen-Längsverbindung 1600 A | busbar connecting terminal 1600 A | 07 | 33 | LVH-L |  |  | 1400 |  |  |  | 30 | [5 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01141.html | www.woehner.com/en/products/01141.html
01147 | Anschlussset, 4-polig, ohne Abdeckung | connection set, 4-pole, without cover | 07 | 51 | M300-L | 600 |  | 420 |  |  |  |  | 22 | 3 cycles (without OPD) @ 600 V AC | 200 | fuse JDDZ Class J 600 A @ 600 V AC | 200 kA / fuse Class J 600A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01145.html | www.woehner.com/en/products/01145.html
01147 | Anschlussset, 4-polig, ohne Abdeckung | connection set, 4-pole, without cover | 07 | 51 | M300-L | 600 |  | 420 |  |  |  |  | 22 | 3 cycles (without OPD) @ 600 V AC | 200 | fuse JDDZ Class J 600 A @ 600 V AC | 200 kA / fuse Class L 800 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01147.html | www.woehner.com/en/products/01147.html
01147 | Anschlussset, 4-polig, ohne Abdeckung | connection set, 4-pole, without cover | 07 | 51 | M300-L | 600 |  | 420 |  |  |  |  | 22 | 3 cycles (without OPD) @ 600 V AC | 200 | fuse JDDZ Class J 600 A @ 600 V AC | 100 kA / fuse Class L 1200 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01147.html | www.woehner.com/en/products/01147.html
01165 | Anschlussklemmenplatte, 3-polig | connection terminal plate, 3 pole | 07 | 48 | M150-L | 600 |  | 285 |  |  |  | 18 | [5 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01147.html | www.woehner.com/en/products/01147.html
01184 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 10x24x1 |  |  |  |  | 800 | 925 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01165.html | www.woehner.com/en/products/01165.html
01185 | Profilklemme | profile terminal | 07 | 30 | H41.2 | 600 |  | 1200 |  |  |  | 30 | [5 empty] | No |  | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01184.html | www.woehner.com/en/products/01184.html
01186 | Profilklemme | profile terminal | 07 | 30 | HH101.2 | 600 |  | 1800 |  |  |  | 25 | [5 empty] | No |  | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01185.html | www.woehner.com/en/products/01185.html
01187 | Dreifach-T-Profilschiene 1140 mm² | triple-T section busbar 1140 mm² | 06 | 92 | HH1140-L |  |  |  | 1800 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01186.html | www.woehner.com/en/products/01186.html
01188 | Dreifach-T-Profilschiene 1140 mm² | triple-T section busbar 1140 mm² | 06 | 92 | HH1140-L |  |  |  | 1800 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01187.html | www.woehner.com/en/products/01187.html
01189 | Dreifach-T-Profilschiene 1140 mm² | triple-T section busbar 1140 mm² | 06 | 92 | HH1140-L |  |  |  | 1800 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01188.html | www.woehner.com/en/products/01188.html
01190 | Doppel-T-Profilschiene 720 mm² | double-T section busbar 720 mm² | 06 | 91 | H720-L |  |  |  | 1400 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01189.html | www.woehner.com/en/products/01189.html
01194 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 6x9x0,8 |  |  |  |  | 255 | 295 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01190.html | www.woehner.com/en/products/01190.html
01196 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 4x15,5x0,8 |  |  |  |  | 295 | 340 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01194.html | www.woehner.com/en/products/01194.html
01203 | Univ.-Leiteranschluss-Klemme | universal conductor terminal | 07 | 18 | 528 | 600 |  | 255 | [11 empty] | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01196.html | www.woehner.com/en/products/01196.html
01204 | Sammelschiene 30 x 10 | busbar 30 x 10 | 06 | 83 | 30x10-L |  |  |  | 630 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01203.html | www.woehner.com/en/products/01203.html
01223 | Doppel-T-Profilschiene 500 mm² | double-T section busbar 500 mm² | 06 | 90 | H500-L |  |  |  | 1200 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01204.html | www.woehner.com/en/products/01204.html
01224 | Doppel-T-Profilschiene 500 mm² | double-T section busbar 500 mm² | 06 | 90 | H500-L |  |  |  | 1200 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01223.html | www.woehner.com/en/products/01223.html
01225 | Doppel-T-Profilschiene 500 mm² | double-T section busbar 500 mm² | 06 | 90 | H500-L |  |  |  | 1200 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01224.html | www.woehner.com/en/products/01224.html
01226 | Doppel-T-Profilschiene 500 mm² | double-T section busbar 500 mm² | 06 | 90 | H500-L |  |  |  | 1200 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01225.html | www.woehner.com/en/products/01225.html
01227 | Dreifach-T-Profilschiene 1140 mm² | triple-T section busbar 1140 mm² | 06 | 92 | HH1140-L |  |  |  | 1800 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01226.html | www.woehner.com/en/products/01226.html
01229 | Doppel-T-Profilschiene 720 mm² | double-T section busbar 720 mm² | 06 | 91 | H720-L |  |  |  | 1400 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01227.html | www.woehner.com/en/products/01227.html
01231 | Sammelschienenträger | busbar support | 06 | 09 | S630-L | 600 | [6 empty] | 30 | 3 cycles (without OPD) @ 600 V AC | 200 | see downloads |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01229.html | www.woehner.com/en/products/01229.html
01232 | Sammelschienenträger | busbar support | 06 | 09 | S640-L | 600 | [6 empty] | 35 | 3 cycles (without OPD) @ 600 V AC | 200 | see downloads |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01231.html | www.woehner.com/en/products/01231.html
01234 | Endabdeckung | end cover | 06 | 27 | 234-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01232.html | www.woehner.com/en/products/01232.html
01236 | Abschottprofil | compartment section | 06 | 27 | C48-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01234.html | www.woehner.com/en/products/01234.html
01237 | Abschottprofil | compartment section | 06 | 27 | C76-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01236.html | www.woehner.com/en/products/01236.html
01238 | Abschottprofil | compartment section | 06 | 27 | C108-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01237.html | www.woehner.com/en/products/01237.html
01240 | Anschlussklemmenplatte, 3-polig | Connection terminal plate, 3 pole | 07 | 42 | 240-L | 600 |  | 175 |  |  |  |  | 10 | 3 cycles (without OPD) @ 600 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01238.html | www.woehner.com/en/products/01238.html
01243 | Anschlussklemmenplatte, 3-polig | connection terminal plate, 3-pole | 07 | 45 | 243-L | 600 |  | 250 |  |  |  |  | 10 | 3 cycles (without OPD) @ 600 V AC | 100 | fuse JDDZ Class J 500 A @ 600 V AC | 100 kA / fuse Class J 600 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01240.html | www.woehner.com/en/products/01240.html
01243 | Anschlussklemmenplatte, 3-polig | connection terminal plate, 3-pole | 07 | 45 | 243-L | 600 |  | 250 |  |  |  |  | 10 | 3 cycles (without OPD) @ 600 V AC | 100 | fuse JDDZ Class J 500 A @ 600 V AC | 50 kA / circuit breaker DIVQ 600 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01243.html | www.woehner.com/en/products/01243.html
01243 | Anschlussklemmenplatte, 3-polig | connection terminal plate, 3-pole | 07 | 45 | 243-L | 600 |  | 250 |  |  |  |  | 10 | 3 cycles (without OPD) @ 600 V AC | 100 | fuse JDDZ Class J 500 A @ 600 V AC | 35 kA / circuit breaker DIVQ 600 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01243.html | www.woehner.com/en/products/01243.html
01243 | Anschlussklemmenplatte, 3-polig | connection terminal plate, 3-pole | 07 | 45 | 243-L | 600 |  | 250 |  |  |  |  | 10 | 3 cycles (without OPD) @ 600 V AC | 100 | fuse JDDZ Class J 500 A @ 600 V AC | 65 kA / circuit breaker DIVQ 400 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01243.html | www.woehner.com/en/products/01243.html
01243 | Anschlussklemmenplatte, 3-polig | connection terminal plate, 3-pole | 07 | 45 | 243-L | 600 |  | 250 |  |  |  |  | 10 | 3 cycles (without OPD) @ 600 V AC | 100 | fuse JDDZ Class J 500 A @ 600 V AC | 100 kA / fuse Class J 500 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01243.html | www.woehner.com/en/products/01243.html
01244 | Sammelschienen-Abdeckung | busbar cover | 06 | 27 | C30x5-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01243.html | www.woehner.com/en/products/01243.html
01245 | Sammelschienen-Abdeckung | busbar cover | 06 | 27 | C30x10-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01244.html | www.woehner.com/en/products/01244.html
01249 | Doppel-T-Profilschiene 720 mm² | double-T section busbar 720 mm² | 06 | 91 | H720-L |  |  |  | 1400 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01245.html | www.woehner.com/en/products/01245.html
01250 | Doppel-T-Profilschiene 500 mm² | double-T section busbar 500 mm² | 06 | 90 | H500-L |  |  |  | 1200 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01249.html | www.woehner.com/en/products/01249.html
01252 | Sammelschienen-Abdeckung | busbar cover | 06 | 27 | CHH-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01250.html | www.woehner.com/en/products/01250.html
01253 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 4x24x1 |  |  |  |  | 470 | 545 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01252.html | www.woehner.com/en/products/01252.html
01255 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 6x24x1 |  |  |  |  | 590 | 680 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01253.html | www.woehner.com/en/products/01253.html
01256 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 6x40x1 |  |  |  |  | 885 | 1020 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01255.html | www.woehner.com/en/products/01255.html
01272 | Sammelschienenträger 3P+N+PE, mit Endabdeckung | busbar support 3 phases + N + E, with end cover | 06 | 09 | S612-L | 600 | [6 empty] | 18 | 3 cycles (without OPD) @ 600 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01256.html | www.woehner.com/en/products/01256.html
01273 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 10x100x1 |  |  |  |  | 2330 | 2690 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01272.html | www.woehner.com/en/products/01272.html
01274 | Schienen-Längsverbindung 2500 A | busbar connecting terminal 2500 A | 07 | 33 | LVHH-L |  |  | 1800 |  |  |  | 35 | [5 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01273.html | www.woehner.com/en/products/01273.html
01275 | Schienen-Längsverbindung 2500 A | busbar connecting terminal 2500 A | 07 | 33 | LVHH-L |  |  | 1800 |  |  |  | 25 | [5 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01274.html | www.woehner.com/en/products/01274.html
01284 | Univ.-Leiteranschluss-Klemme | universal conductor terminal | 07 | 03 | 521 | 600 |  | 65 | [11 empty] | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01275.html | www.woehner.com/en/products/01275.html
01285 | Univ.-Leiteranschluss-Klemme | universal conductor terminal | 07 | 06 | 522 | 600 |  | 115 | [11 empty] | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01284.html | www.woehner.com/en/products/01284.html
01287 | Univ.-Leiteranschluss-Klemme | universal conductor terminal | 07 | 12 | 523 | 600 |  | 175 | [11 empty] | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01285.html | www.woehner.com/en/products/01285.html
01289 | Univ.-Leiteranschluss-Klemme | universal conductor terminal | 07 | 03 | 525 | 600 |  | 65 | [11 empty] | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01287.html | www.woehner.com/en/products/01287.html
01290 | Univ.-Leiteranschluss-Klemme | universal conductor terminal | 07 | 06 | 526 | 600 |  | 115 | [11 empty] | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01289.html | www.woehner.com/en/products/01289.html
01292 | Univ.-Leiteranschluss-Klemme | universal conductor terminal | 07 | 12 | 527 | 600 |  | 175 | [11 empty] | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01290.html | www.woehner.com/en/products/01290.html
01300 | Einzelabdeckung der Klemmen | single cover for terminals | 07 | 39 | 240 | [12 empty] | Yes |  | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01292.html | www.woehner.com/en/products/01292.html
01301 | Einzelabdeckung der Klemmen | single cover for terminals | 07 | 39 | 243 | [12 empty] | Yes |  | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01300.html | www.woehner.com/en/products/01300.html
01314 | Abdeckprofil, compact | Cover profile, compact | 06 | 27 | C314-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01301.html | www.woehner.com/en/products/01301.html
01317 | Halter für Abdeckprofile | Mount for cover section | 06 | 27 | C317-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01314.html | www.woehner.com/en/products/01314.html
01318 | Spreizklemme | brace terminal | 07 | 20 | 518 | 600 |  | 310 |  |  |  | 25 | [5 empty] | No |  | UL recognized | E123577 | NMTR2 | [6 empty] | www.woehner.com/de/products/01317.html | www.woehner.com/en/products/01317.html
01319 | Spreizklemme | brace terminal | 07 | 20 | 519 | 600 |  | 800 |  |  |  | 25 | [5 empty] | No |  | UL recognized | E123577 | NMTR2 | [6 empty] | www.woehner.com/de/products/01318.html | www.woehner.com/en/products/01318.html
01320 | Halter für Abdeckprofile | Mount for cover section | 06 | 27 | C026-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | [6 empty] | www.woehner.com/de/products/01319.html | www.woehner.com/en/products/01319.html
01323 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 8x24x1 |  |  |  |  | 700 | 810 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01320.html | www.woehner.com/en/products/01320.html
01324 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 5x63x1 |  |  |  |  | 1165 | 1345 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01323.html | www.woehner.com/en/products/01323.html
01343 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 8x50x1 |  |  |  |  | 1225 | 1410 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01324.html | www.woehner.com/en/products/01324.html
01356 | Sammelschienenträger PE/N | PE/N-support | 06 | 06 | S356-L | 600 | [11 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01343.html | www.woehner.com/en/products/01343.html
01357 | UL-Sammelschienenträger | universal busbar support UL | 06 | 12 | S62015-L | 600 | [6 empty] | 18 | 3 cycles (without OPD) @ 600 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01356.html | www.woehner.com/en/products/01356.html
01358 | Distanzstück | spacer | 06 | 30 | D620-L | 600 | [11 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01357.html | www.woehner.com/en/products/01357.html
01359 | Distanzstück | spacer | 06 | 30 | D620-L | 600 | [11 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01358.html | www.woehner.com/en/products/01358.html
01360 | UL-Trennstegeset, 3-polig | Set of phase separators for UL installation, 3-pole | 06 | 27 | P620-L | 600 | [11 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01359.html | www.woehner.com/en/products/01359.html
01361 | UL-Trennstegeset, 3-polig | Set of phase separators for UL installation, 3-pole | 06 | 27 | P620-L | 600 | [11 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01360.html | www.woehner.com/en/products/01360.html
01362 | UL-Trennstegeset, 3-polig | Set of phase separators for UL installation, 3-pole | 06 | 27 | P620-L | 600 | [11 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01361.html | www.woehner.com/en/products/01361.html
01370 | Anschluss-Set, 3-polig L1-L2-L3 | connection set, 3-pole L1-L2-L3 | 07 | 45 | M120-L | 600 |  | 200 |  |  |  | 18 | [5 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01362.html | www.woehner.com/en/products/01362.html
01374 | Distanzstück | spacer | 06 | 30 | D612-L | 600 | [11 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01370.html | www.woehner.com/en/products/01370.html
01401 | Anschlussklemmenplatte, 3-polig | Connection terminal plate, 3 pole | 07 | 42 | 240C-L | 600 |  | 175 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01374.html | www.woehner.com/en/products/01374.html
01413 | Abdeckkappe, 3-polig | cover cap, 3-pole | 07 | 36 | 412 | [14 empty] | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01401.html | www.woehner.com/en/products/01401.html
01417 | Abdeckprofil | cover section | 06 | 27 | C60.2-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | [6 empty] | www.woehner.com/de/products/01413.html | www.woehner.com/en/products/01413.html
01420 | Systemabschottung, rückseitig | system shrouding, rear | 06 | 27 | 01420000A | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01417.html | www.woehner.com/en/products/01417.html
01421 | Distanzstück | spacer | 06 | 27 | D185 | 1000 | [13 empty] | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01418.html | www.woehner.com/en/products/01418.html
01430 | Universal-Sammelschienenträger | universal busbar support | 06 | 24 | S185-A120 | 1000 | 1000 | [5 empty] | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01420.html | www.woehner.com/en/products/01420.html
01431 | Endabdeckung für Sammelschienenträger 01430 | end cover for busbar support 01430 | 06 | 27 | 01431000A | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01421.html | www.woehner.com/en/products/01421.html
01432 | Mittenabdeckung für Sammelschienenträger 01430 | centre cover for busbar support 01430 | 06 | 27 | 01432000A | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01430.html | www.woehner.com/en/products/01430.html
01433 | CrossLink®-Berührungsschutzmodul | CrossLink® touch-safe protection cover module | 06 | 27 | CL185-A50 | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01431.html | www.woehner.com/en/products/01431.html
01434 | CrossLink®-Berührungsschutzmodul | CrossLink® touch-safe protection cover module | 06 | 27 | CL185-A100 | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01432.html | www.woehner.com/en/products/01432.html
01436 | Systemabschottung, rückseitig | system shrouding, rear | 06 | 27 | 01436000A | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01433.html | www.woehner.com/en/products/01433.html
01437 | Abdeckhaube inkl. rückseitigem Berührungsschutz | cover cap incl. rear touch protection cover | 07 | 36 | C185-B | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01434.html | www.woehner.com/en/products/01434.html
01440 | Abschlussprofil | completion section | 06 | 27 | 01440000A | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01436.html | www.woehner.com/en/products/01436.html
01441 | Anschlussmodul | connection module | 07 | 54 | CR185-A2x300 | 1000 | 1000 | 840 |  |  |  |  | 35 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01437.html | www.woehner.com/en/products/01437.html
01442 | Anschlussmodul | connection module | 07 | 54 | CR185-A80 | 1000 |  | 1400 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01440.html | www.woehner.com/en/products/01440.html
01443 | Anschlussmodul | connection module | 07 | 54 | CR185-A2x12 | 1000 |  | 1520 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01441.html | www.woehner.com/en/products/01441.html
01444 | Abschlussprofil | completion section | 06 | 27 | 01444000A | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01442.html | www.woehner.com/en/products/01442.html
01480 | Schienen-Längsverbindung | longitudinal busbar connector | 07 | 33 | CR185-C40 | 1000 | 1000 | 700 |  |  |  |  | 42 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01443.html | www.woehner.com/en/products/01443.html
01481 | Schienen-Längsverbindung | longitudinal busbar connector | 07 | 33 | CR185-C60 | 1000 | 1000 | 1100 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01444.html | www.woehner.com/en/products/01444.html
01482 | Berührungsschutzabdeckung für Längsverbinder | touch-safe protection shroud for longitudinal connectors | 06 | 27 | C185-C | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01480.html | www.woehner.com/en/products/01480.html
01485 | Universal-Sammelschienenträger | universal busbar support | 06 | 12 | 485 | 600 | [13 empty] | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01481.html | www.woehner.com/en/products/01481.html
01489 | Sammelschienenträger PE/N | PE/N-support | 06 | 03 | 489 | 600 | [13 empty] | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01482.html | www.woehner.com/en/products/01482.html
01508 | UL-Sammelschienenträger | universal busbar support UL | 06 | 09 | S620-L | 600 | [6 empty] | 22 | 3 cycles (without OPD) @ 600 V AC | 100 | see mounting instruction |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01485.html | www.woehner.com/en/products/01485.html
01509 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 10x50x1 |  |  |  |  | 1375 | 1585 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01489.html | www.woehner.com/en/products/01489.html
01510 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 10x63x1 |  |  |  |  | 1630 | 1875 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01508.html | www.woehner.com/en/products/01508.html
01513 | Profilklemme | profile terminal | 07 | 30 | HH41.2 | 600 |  | 1200 |  |  |  | 25 | [5 empty] | No |  | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01509.html | www.woehner.com/en/products/01509.html
01515 | Bodenplatte UL | base plate UL | 06 | 27 | B620-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01510.html | www.woehner.com/en/products/01510.html
01518 | Bodenplatte UL | base plate UL | 06 | 27 | B620-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01513.html | www.woehner.com/en/products/01513.html
01537 | Anschlussset, 3-polig, ohne Abdeckung | connection set, 3-pole, without cover | 07 | 51 | M300-L | 600 |  | 420 |  |  |  |  | 22 | 3 cycles (without OPD) @ 600 V AC | 200 | fuse JDDZ Class J 600 A @ 600 V AC | 100 kA / fuse Class L 1200 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01515.html | www.woehner.com/en/products/01515.html
01537 | Anschlussset, 3-polig, ohne Abdeckung | connection set, 3-pole, without cover | 07 | 51 | M300-L | 600 |  | 420 |  |  |  |  | 22 | 3 cycles (without OPD) @ 600 V AC | 200 | fuse JDDZ Class J 600 A @ 600 V AC | 200 kA / fuse Class L 800 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01518.html | www.woehner.com/en/products/01518.html
01537 | Anschlussset, 3-polig, ohne Abdeckung | connection set, 3-pole, without cover | 07 | 51 | M300-L | 600 |  | 420 |  |  |  |  | 22 | 3 cycles (without OPD) @ 600 V AC | 200 | fuse JDDZ Class J 600 A @ 600 V AC | 200 kA / fuse Class J 600A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01537.html | www.woehner.com/en/products/01537.html
01538 | Anschlussset, 3-polig, ohne Abdeckung | connection set, 3-pole, without cover | 07 | 51 | M3210-L | 600 |  | 800 |  |  |  |  | 25 | 3 cycles (without OPD) @ 600 V AC | 200 | fuse JDDZ Class J 600 A @ 600 V AC |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01537.html | www.woehner.com/en/products/01537.html
01539 | Abdeckkappe, 3-polig | cover cap, 3-pole | 07 | 36 | CTC60-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01537.html | www.woehner.com/en/products/01537.html
01540 | Abdeckkappe, 3-polig | cover cap, 3-pole | 07 | 36 | CTC60-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01538.html | www.woehner.com/en/products/01538.html
01554 | Abdeckprofil, für 3-polige Systeme | compartment section, for 3-pole systems | 07 | 36 | C60.1-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01539.html | www.woehner.com/en/products/01539.html
01555 | Abdeckprofil | cover section | 07 | 36 | C60.2-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01540.html | www.woehner.com/en/products/01540.html
01562 | Anschlussmodul 16 mm², 3-polig | connection module 16 mm², 3-pole | 07 | 40 | M16C-L | 600 |  | 48 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 50 | fuse JDDZ Class J 60 A @ 600 V AC |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01554.html | www.woehner.com/en/products/01554.html
01563 | Anschlussmodul 16 mm², 3-polig | connection module 16 mm², 3-pole | 07 | 40 | M16-L | 600 |  | 48 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 50 | fuse JDDZ Class J 60 A @ 600 V AC |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01555.html | www.woehner.com/en/products/01555.html
01569 | Anschlussklemmenplatte, 3-polig | Connection terminal plate, 3 pole | 07 | 42 | 240-L | 600 |  | 175 |  |  |  |  | 10 | 3 cycles (without OPD) @ 600 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01562.html | www.woehner.com/en/products/01562.html
01570 | Anschlussklemmenplatte, 3-polig | connection terminal plate, 3-pole | 07 | 45 | 243-L | 600 |  | 255 |  |  |  |  | 10 | 3 cycles (without OPD) @ 600 V AC | 100 | fuse JDDZ Class J 500 A @ 600 V AC | 100 kA / fuse Class J 500 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01563.html | www.woehner.com/en/products/01563.html
01570 | Anschlussklemmenplatte, 3-polig | connection terminal plate, 3-pole | 07 | 45 | 243-L | 600 |  | 255 |  |  |  |  | 10 | 3 cycles (without OPD) @ 600 V AC | 100 | fuse JDDZ Class J 500 A @ 600 V AC | 35 kA / circuit breaker DIVQ 600 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01569.html | www.woehner.com/en/products/01569.html
01570 | Anschlussklemmenplatte, 3-polig | connection terminal plate, 3-pole | 07 | 45 | 243-L | 600 |  | 255 |  |  |  |  | 10 | 3 cycles (without OPD) @ 600 V AC | 100 | fuse JDDZ Class J 500 A @ 600 V AC | 100 kA / fuse Class J 600 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01570.html | www.woehner.com/en/products/01570.html
01570 | Anschlussklemmenplatte, 3-polig | connection terminal plate, 3-pole | 07 | 45 | 243-L | 600 |  | 255 |  |  |  |  | 10 | 3 cycles (without OPD) @ 600 V AC | 100 | fuse JDDZ Class J 500 A @ 600 V AC | 50 kA / circuit breaker DIVQ 600 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01570.html | www.woehner.com/en/products/01570.html
01570 | Anschlussklemmenplatte, 3-polig | connection terminal plate, 3-pole | 07 | 45 | 243-L | 600 |  | 255 |  |  |  |  | 10 | 3 cycles (without OPD) @ 600 V AC | 100 | fuse JDDZ Class J 500 A @ 600 V AC | 65 kA / circuit breaker DIVQ 400 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01570.html | www.woehner.com/en/products/01570.html
01573 | Endabdeckung | end cover | 06 | 27 | 511-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01570.html | www.woehner.com/en/products/01570.html
01583 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 10x15,5x0,8 |  |  |  |  | 510 | 590 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01570.html | www.woehner.com/en/products/01570.html
01590 | Abdeckkappe, 3-polig | cover cap, 3-pole | 07 | 36 | 502 | [14 empty] | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01573.html | www.woehner.com/en/products/01573.html
01592 | Anschlussmodul 16 mm², 3-polig | connection module 16 mm², 3-pole | 07 | 40 | CR22-A | 600 |  | 48 |  |  |  |  | 6 | 3 cycles (without OPD) @ 600 V AC | 50 | fuse JDDZ Class J 60 A @ 600 V AC |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01583.html | www.woehner.com/en/products/01583.html
01593 | Anschlussmodul 50 mm², 3-polig | connection module 50 mm², 3-pole | 07 | 42 | CR45-A | 600 |  | 100 |  |  |  |  | 10 |  | 100 |  | 100 kA / Class J 175 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01590.html | www.woehner.com/en/products/01590.html
01593 | Anschlussmodul 50 mm², 3-polig | connection module 50 mm², 3-pole | 07 | 42 | CR45-A | 600 |  | 100 |  |  |  |  | 10 |  | 100 |  | 100 kA / MCCB DIVQ/7 100 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01592.html | www.woehner.com/en/products/01592.html
01593 | Anschlussmodul 50 mm², 3-polig | connection module 50 mm², 3-pole | 07 | 42 | CR45-A | 600 |  | 100 |  |  |  |  | 10 |  | 100 |  | 65 kA / MCCB DIVQ/7 100 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01593.html | www.woehner.com/en/products/01593.html
01596 | Abdeckkappe, 3-polig | cover cap, 3-pole | 07 | 36 | CTC60-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01593.html | www.woehner.com/en/products/01593.html
01597 | Abdeckkappe, 4-polig | cover cap, 4-pole | 07 | 36 | CTC60-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01593.html | www.woehner.com/en/products/01593.html
01599 | Abdeckprofil, für 4-polige Systeme | front cover section, for 4-pole systems | 07 | 36 | C60.1-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01596.html | www.woehner.com/en/products/01596.html
01601 | Sammelschienenträger PE/N | PE/N-support | 06 | 03 | S489-L | 600 | [11 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR8 | [5 empty] | www.woehner.com/de/products/01597.html | www.woehner.com/en/products/01597.html
01608 | Doppel-T-Profilschiene 720 mm² | double-T section busbar 720 mm² | 06 | 91 | H720-L |  |  |  | 1400 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01599.html | www.woehner.com/en/products/01599.html
01609 | Doppel-T-Profilschiene 500 mm² | double-T section busbar 500 mm² | 06 | 90 | H500-L |  |  |  | 1200 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01601.html | www.woehner.com/en/products/01601.html
01611 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 5x24x1 |  |  |  |  | 535 | 615 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01608.html | www.woehner.com/en/products/01608.html
01612 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 5x32x1 |  |  |  |  | 670 | 775 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01609.html | www.woehner.com/en/products/01609.html
01613 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 10x32x1 |  |  |  |  | 985 | 1135 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01611.html | www.woehner.com/en/products/01611.html
01614 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 5x40x1 |  |  |  |  | 805 | 925 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01612.html | www.woehner.com/en/products/01612.html
01615 | Lamellierte Kupferschiene, blank, isoliert | flexible copper busbar, plain, insulated | 06 | 81 | 10x40x1 |  |  |  |  | 1160 | 1340 | [6 empty] | Yes |  | UL recognized | E197039 | QEUY2 | QEUY8 | E481423 | AVLV2 |  |  |  | www.woehner.com/de/products/01613.html | www.woehner.com/en/products/01613.html
01618 | Sammelschiene 12 x 5 | busbar 12 x 5 | 06 | 82 | 12x5-L |  |  |  | 150 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01614.html | www.woehner.com/en/products/01614.html
01620 | Sammelschiene 20 x 5 | busbar 20 x 5 | 06 | 82 | 20x5-L |  |  |  | 362 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01615.html | www.woehner.com/en/products/01615.html
01622 | Sammelschiene 30 x 5 | busbar 30 x 5 | 06 | 82 | 30x5-L |  |  |  | 500 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01618.html | www.woehner.com/en/products/01618.html
01623 | Sammelschiene 12 x 10 | busbar 12 x 10 | 06 | 83 | 12x10-L |  |  |  | 300 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01620.html | www.woehner.com/en/products/01620.html
01624 | Sammelschiene 20 x 10 | busbar 20 x 10 | 06 | 83 | 20x10-L |  |  |  | 564 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01622.html | www.woehner.com/en/products/01622.html
01625 | Sammelschiene 30 x 10 | busbar 30 x 10 | 06 | 83 | 30x10-L |  |  |  | 630 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01623.html | www.woehner.com/en/products/01623.html
01626 | Sammelschiene 40 x 10 | busbar 40 x 10 | 06 | 84 | 40x10-L |  |  |  | 700 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01624.html | www.woehner.com/en/products/01624.html
01628 | Sammelschiene 60 x 10 | busbar 60 x 10 | 06 | 84 | 60x10-L |  |  |  | 1100 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01625.html | www.woehner.com/en/products/01625.html
01756 | Abdeckkappe, 3-polig | cover cap, 3-pole | 07 | 36 | 512-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01626.html | www.woehner.com/en/products/01626.html
01757 | Abdeckkappe, 3-polig | cover cap, 3-pole | 07 | 36 | 513-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01628.html | www.woehner.com/en/products/01628.html
01759 | Spreizklemme | brace terminal | 07 | 25 | 530 | 600 |  | 800 |  |  |  | 25 | [5 empty] | No |  | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01756.html | www.woehner.com/en/products/01756.html
01760 | Spreizklemme | brace terminal | 07 | 25 | 529 | 600 |  | 420 |  |  |  | 25 | [5 empty] | No |  | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01757.html | www.woehner.com/en/products/01757.html
01765 | Sammelschiene 80 x 10 | busbar 80 x 10 | 06 | 84 | 80x10-L |  |  |  | 1300 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01759.html | www.woehner.com/en/products/01759.html
01766 | Sammelschiene 100 x 10 | busbar 100 x 10 | 06 | 84 | 100x10-L |  |  |  | 1550 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01760.html | www.woehner.com/en/products/01760.html
01767 | Sammelschiene 120 x 10 | busbar 120 x 10 | 06 | 84 | 120x10-L |  |  |  | 1800 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01765.html | www.woehner.com/en/products/01765.html
01774 | Sammelschienenträger | busbar support | 06 | 15 | 497 | 600 | [13 empty] | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01766.html | www.woehner.com/en/products/01766.html
01823 | Schienen-Längsverbindung 630 A | busbar connecting terminal 630 A | 07 | 33 | LV30-L |  |  | 756 |  |  |  | 25 | [5 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01767.html | www.woehner.com/en/products/01767.html
01827 | Schienen-Längsverbindung 1600 A | busbar connecting terminal 1600 A | 07 | 33 | LVH-L |  |  | 1400 |  |  |  | 30 | [5 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01774.html | www.woehner.com/en/products/01774.html
01829 | Schienen-Längsverbindung 1600 A | busbar connecting terminal 1600 A | 07 | 33 | LVH-L |  |  | 1400 |  |  |  | 45 | [5 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01775.html | www.woehner.com/en/products/01775.html
01831 | Doppel-T-Profilschiene 720 mm² | double-T section busbar 720 mm² | 06 | 91 | H720-L |  |  |  | 1400 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01823.html | www.woehner.com/en/products/01823.html
01838 | Doppel-T-Profilschiene 720 mm² | double-T section busbar 720 mm² | 06 | 91 | H720-L |  |  |  | 1400 | [8 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01827.html | www.woehner.com/en/products/01827.html
01886 | Schienen-Längsverbindung 630 A | busbar connecting terminal 630 A | 07 | 33 | LV30-L |  |  | 756 |  |  |  | 25 | [5 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01829.html | www.woehner.com/en/products/01829.html
01906 | Profilklemme | profile terminal | 07 | 30 | H51.1 | 600 |  | 1200 |  |  |  | 25 | [5 empty] | No |  | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01831.html | www.woehner.com/en/products/01831.html
01907 | Profilklemme | profile terminal | 07 | 30 | H64.1 | 600 |  | 1400 |  |  |  | 25 | [5 empty] | No |  | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01838.html | www.woehner.com/en/products/01838.html
01911 | Profilklemme | profile terminal | 07 | 30 | H64.2 | 600 |  | 1400 |  |  |  | 25 | [5 empty] | No |  | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01886.html | www.woehner.com/en/products/01886.html
01915 | Sammelschienenträger | busbar support | 06 | 18 | 499 | 600 | [13 empty] | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01906.html | www.woehner.com/en/products/01906.html
01934 | Profilklemme | profile terminal | 07 | 30 | H81.2 | 600 |  | 1800 |  |  |  | 25 | [5 empty] | No |  | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01907.html | www.woehner.com/en/products/01907.html
01935 | Profilklemme | profile terminal | 07 | 30 | H101.2 | 600 |  | 1800 |  |  |  | 25 | [5 empty] | No |  | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01911.html | www.woehner.com/en/products/01911.html
01936 | Profilklemme | profile terminal | 07 | 30 | H51.2 | 600 |  | 1200 |  |  |  | 25 | [5 empty] | No |  | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/01934.html | www.woehner.com/en/products/01934.html
01990 | Schienen-Längsverbindung 630 A | busbar connecting terminal 630 A | 07 | 33 | LV30-L |  |  | 756 |  |  |  | 25 | [5 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/01935.html | www.woehner.com/en/products/01935.html
03214 | Sicherungseinsatz 70 A, fast acting (flink) | fuse link 70 A, fast acting | 22 | 34 | JKS | 600 |  | 70 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/01936.html | www.woehner.com/en/products/01936.html
03215 | Sicherungseinsatz 80 A, fast acting (flink) | fuse link 80 A, fast acting | 22 | 34 | JKS | 600 |  | 80 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/01990.html | www.woehner.com/en/products/01990.html
03217 | Sicherungseinsatz 100 A, fast acting (flink) | fuse link 100 A, fast acting | 22 | 34 | JKS | 600 |  | 100 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/03214.html | www.woehner.com/en/products/03214.html
03219 | Sicherungseinsatz 125 A, fast acting (flink) | fuse link 125 A, fast acting | 22 | 34 | A4J | 600 | 300 | 125 |  |  |  | 200 | [7 empty] | UL recognized | E2137 | JDDZ2 | [6 empty] | www.woehner.com/de/products/03215.html | www.woehner.com/en/products/03215.html
03220 | Sicherungseinsatz 150 A, fast acting (flink) | fuse link 150 A, fast acting | 22 | 34 | A4J | 600 | 300 | 150 |  |  |  | 200 | [7 empty] | UL recognized | E2137 | JDDZ2 | [6 empty] | www.woehner.com/de/products/03217.html | www.woehner.com/en/products/03217.html
03221 | Sicherungseinsatz 175 A, fast acting (flink) | fuse link 175 A, fast acting | 22 | 34 | A4J | 600 | 300 | 175 |  |  |  | 200 | [7 empty] | UL recognized | E2137 | JDDZ2 | [6 empty] | www.woehner.com/de/products/03219.html | www.woehner.com/en/products/03219.html
03222 | Sicherungseinsatz 200 A, fast acting (flink) | fuse link 200 A, fast acting | 22 | 34 | A4J | 600 | 300 | 200 |  |  |  | 200 | [7 empty] | UL recognized | E2137 | JDDZ2 | [6 empty] | www.woehner.com/de/products/03220.html | www.woehner.com/en/products/03220.html
03224 | Sicherungseinsatz 250 A, fast acting (flink) | fuse link 250 A, fast acting | 22 | 34 | JKS | 600 |  | 250 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/03221.html | www.woehner.com/en/products/03221.html
03225 | Sicherungseinsatz 300 A, fast acting (flink) | fuse link 300 A, fast acting | 22 | 34 | JKS | 600 |  | 300 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/03222.html | www.woehner.com/en/products/03222.html
03226 | Sicherungseinsatz 350 A, fast acting (flink) | fuse link 350 A, fast acting | 22 | 34 | JKS | 600 |  | 350 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/03224.html | www.woehner.com/en/products/03224.html
03227 | Sicherungseinsatz 400 A, fast acting (flink) | fuse link 400 A, fast acting | 22 | 34 | JKS | 600 |  | 400 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/03225.html | www.woehner.com/en/products/03225.html
03228 | Sicherungseinsatz 70 A, time delay (träge) | fuse link 70 A, time delay | 22 | 33 | LPJ | 600 | 300 | 70 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/03226.html | www.woehner.com/en/products/03226.html
03229 | Sicherungseinsatz 80 A, time delay (träge) | fuse link 80 A, time delay | 22 | 33 | LPJ | 600 | 300 | 80 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/03227.html | www.woehner.com/en/products/03227.html
03230 | Sicherungseinsatz 90 A, time delay (träge) | fuse link 90 A, time delay | 22 | 33 | LPJ | 600 | 300 | 90 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/03228.html | www.woehner.com/en/products/03228.html
03231 | Sicherungseinsatz 100 A, time delay (träge) | fuse link 100 A, time delay | 22 | 33 | LPJ | 600 | 300 | 100 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/03229.html | www.woehner.com/en/products/03229.html
03233 | Sicherungseinsatz 125 A, time delay (träge) | fuse link 125 A, time delay | 22 | 33 | LPJ | 600 | 300 | 125 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/03230.html | www.woehner.com/en/products/03230.html
03234 | Sicherungseinsatz 150 A, time delay (träge) | fuse link 150 A, time delay | 22 | 33 | LPJ | 600 | 300 | 150 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/03231.html | www.woehner.com/en/products/03231.html
03235 | Sicherungseinsatz 175 A, time delay (träge) | fuse link 175 A, time delay | 22 | 33 | LPJ | 600 | 300 | 175 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/03233.html | www.woehner.com/en/products/03233.html
03236 | Sicherungseinsatz 200 A, time delay (träge) | fuse link 200 A, time delay | 22 | 33 | LPJ | 600 | 300 | 200 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/03234.html | www.woehner.com/en/products/03234.html
03238 | Sicherungseinsatz 250 A, time delay (träge) | fuse link 250 A, time delay | 22 | 33 | LPJ | 600 | 300 | 250 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/03235.html | www.woehner.com/en/products/03235.html
03239 | Sicherungseinsatz 300 A, time delay (träge) | fuse link 300 A, time delay | 22 | 33 | LPJ | 600 | 300 | 300 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/03236.html | www.woehner.com/en/products/03236.html
03240 | Sicherungseinsatz 350 A, time delay (träge) | fuse link 350 A, time delay | 22 | 33 | LPJ | 600 | 300 | 350 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/03238.html | www.woehner.com/en/products/03238.html
03241 | Sicherungseinsatz 400 A, time delay (träge) | fuse link 400 A, time delay | 22 | 33 | LPJ | 600 | 300 | 400 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/03239.html | www.woehner.com/en/products/03239.html
03289 | NH-Sicherungs-Unterteil 250 A, Aufbau, für PV | NH fuse-base 250 A, panel mounting, for PV | 10 | 07 | PVH-NH1XL-30 |  | 1500 | 250 |  |  |  | 15 | [7 empty] | UL recognized | E342576 | IZMR2 | [6 empty] | www.woehner.com/de/products/03240.html | www.woehner.com/en/products/03240.html
03290 | NH-Sicherungs-Unterteil 250 A, Aufbau, für PV | NH fuse-base 250 A, panel mounting, for PV | 10 | 07 | PVH-NH1XL |  | 1500 | 250 |  |  |  | 15 | [7 empty] | UL recognized | E342576 | IZMR2 | [6 empty] | www.woehner.com/de/products/03241.html | www.woehner.com/en/products/03241.html
03293 | NH-Sicherungs-Unterteil 600 A, Aufbau, für PV | NH fuse-base 600 A, panel mounting, for PV | 10 | 13 | PVH-NH2XL/3L |  | 1500 | 600 |  |  |  | 15 | [7 empty] | UL recognized | E342576 | IZMR2 | [6 empty] | www.woehner.com/de/products/03289.html | www.woehner.com/en/products/03289.html
03294 | NH-Sicherungs-Unterteil 600 A, Aufbau, für PV | NH fuse-base 600 A, panel mounting, for PV | 10 | 13 | PVH-NH2XL/3L-40 |  | 1500 | 600 |  |  |  | 15 | [7 empty] | UL recognized | E342576 | IZMR2 | [6 empty] | www.woehner.com/de/products/03290.html | www.woehner.com/en/products/03290.html
11225 | Basissystem 125 A | basic system 125 A | 06 | 50 | CB225-24x7 | 600 | 600 | 100 |  |  |  |  | 10 |  | 100 |  | 100 kA / Class J 175 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/03293.html | www.woehner.com/en/products/03293.html
11225 | Basissystem 125 A | basic system 125 A | 06 | 50 | CB225-24x7 | 600 | 600 | 100 |  |  |  |  | 10 |  | 100 |  | 100 kA / MCCB DIVQ/7 100 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/03294.html | www.woehner.com/en/products/03294.html
11225 | Basissystem 125 A | basic system 125 A | 06 | 50 | CB225-24x7 | 600 | 600 | 100 |  |  |  |  | 10 |  | 100 |  | 65 kA / MCCB DIVQ/7 100 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/11225.html | www.woehner.com/en/products/11225.html
11405 | Basissystem 125 A | basic system 125 A | 06 | 50 | CB405-24x7 | 600 | 600 | 100 |  |  |  |  | 10 |  | 100 |  | 100 kA / Class J 175 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/11225.html | www.woehner.com/en/products/11225.html
11405 | Basissystem 125 A | basic system 125 A | 06 | 50 | CB405-24x7 | 600 | 600 | 100 |  |  |  |  | 10 |  | 100 |  | 100 kA / MCCB DIVQ/7 100 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/11225.html | www.woehner.com/en/products/11225.html
11405 | Basissystem 125 A | basic system 125 A | 06 | 50 | CB405-24x7 | 600 | 600 | 100 |  |  |  |  | 10 |  | 100 |  | 65 kA / MCCB DIVQ/7 100 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/11225.html | www.woehner.com/en/products/11225.html
31039 | Anschlussklemme, frontaler Anschluss | connection terminal, front connection | 07 | 26 | CTB-T35.1 | 1000 | 1000 | 115 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/11405.html | www.woehner.com/en/products/11405.html
31042 | Endkappe | end cap | 06 | 30 | CTB-C1.1 | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/11405.html | www.woehner.com/en/products/11405.html
31110 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 17 | 06 | AES10x38 | 600 | 600 | 30 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/11405.html | www.woehner.com/en/products/11405.html
31111 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 17 | 06 | AES10x38 | 600 | 600 | 30 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/11405.html | www.woehner.com/en/products/11405.html
31112 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 17 | 06 | AES10x38 | 600 | 600 | 30 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31039.html | www.woehner.com/en/products/31039.html
31113 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 17 | 06 | AES10x38 | 600 | 600 | 30 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31042.html | www.woehner.com/en/products/31042.html
31114 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 17 | 06 | AES10x38 | 600 | 600 | 30 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31110.html | www.woehner.com/en/products/31110.html
31115 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 17 | 09 | AES14x51 | 600 | 600 | 50 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31111.html | www.woehner.com/en/products/31111.html
31116 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 17 | 09 | AES14x51 | 600 | 600 | 50 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31112.html | www.woehner.com/en/products/31112.html
31117 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 17 | 09 | AES14x51 | 600 | 600 | 50 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31113.html | www.woehner.com/en/products/31113.html
31118 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 17 | 09 | AES14x51 | 600 | 600 | 50 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31114.html | www.woehner.com/en/products/31114.html
31119 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 17 | 09 | AES14x51 | 600 | 600 | 50 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31115.html | www.woehner.com/en/products/31115.html
31120 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 17 | 12 | AES22x58 | 600 | 600 | 80 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31116.html | www.woehner.com/en/products/31116.html
31121 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 17 | 12 | AES22x58 | 600 | 600 | 80 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31117.html | www.woehner.com/en/products/31117.html
31122 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 17 | 12 | AES22x58 | 600 | 600 | 80 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31118.html | www.woehner.com/en/products/31118.html
31123 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 17 | 12 | AES22x58 | 600 | 600 | 80 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31119.html | www.woehner.com/en/products/31119.html
31124 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 17 | 12 | AES22x58 | 600 | 600 | 80 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31120.html | www.woehner.com/en/products/31120.html
31130 | Halter für zylindrische Sicherungen, mit LED | holder for cylindrical fuses, with LED | 17 | 06 | AES10x38 | 600 | 600 | 30 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31121.html | www.woehner.com/en/products/31121.html
31132 | Halter für zylindrische Sicherungen, mit LED | holder for cylindrical fuses, with LED | 17 | 06 | AES10x38 | 600 | 600 | 30 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31122.html | www.woehner.com/en/products/31122.html
31133 | Halter für zylindrische Sicherungen, mit LED | holder for cylindrical fuses, with LED | 17 | 06 | AES10x38 | 600 | 600 | 30 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31123.html | www.woehner.com/en/products/31123.html
31135 | Halter für zylindrische Sicherungen, mit LED | holder for cylindrical fuses, with LED | 17 | 09 | AES14x51 | 600 | 600 | 50 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31124.html | www.woehner.com/en/products/31124.html
31138 | Halter für zylindrische Sicherungen, mit LED | holder for cylindrical fuses, with LED | 17 | 09 | AES14x51 | 600 | 600 | 50 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31130.html | www.woehner.com/en/products/31130.html
31140 | Halter für zylindrische Sicherungen, mit LED | holder for cylindrical fuses, with LED | 17 | 12 | AES22x58 | 600 | 600 | 80 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31132.html | www.woehner.com/en/products/31132.html
31143 | Halter für zylindrische Sicherungen, mit LED | holder for cylindrical fuses, with LED | 17 | 12 | AES22x58 | 600 | 600 | 80 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31133.html | www.woehner.com/en/products/31133.html
31168 | Halter für zylindrische Sicherungen, Nullleiter links | holder for cylindrical fuses, N left mounted | 17 | 09 | AES14x51 | 600 | 600 | 50 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31135.html | www.woehner.com/en/products/31135.html
31171 | Halter für zylindrische Sicherungen, Nullleiter links | holder for cylindrical fuses, N left mounted | 17 | 12 | AES22x58 | 600 | 600 | 80 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31138.html | www.woehner.com/en/products/31138.html
31205 | Zylindr. Sicherungseinsatz 1 A | cylindr. fuse link 1 A | 22 | 22 |  | 700 | [13 empty] | UL recognized | E180276 | JFHR2 | [6 empty] | www.woehner.com/de/products/31140.html | www.woehner.com/en/products/31140.html
31206 | Zylindr. Sicherungseinsatz 2 A | cylindr. fuse link 2 A | 22 | 22 |  | 700 | [13 empty] | UL recognized | E180276 | JFHR2 | [6 empty] | www.woehner.com/de/products/31143.html | www.woehner.com/en/products/31143.html
31207 | Zylindr. Sicherungseinsatz 4 A | cylindr. fuse link 4 A | 22 | 22 |  | 700 | [13 empty] | UL recognized | E180276 | JFHR2 | [6 empty] | www.woehner.com/de/products/31168.html | www.woehner.com/en/products/31168.html
31208 | Zylindr. Sicherungseinsatz 6 A | cylindr. fuse link 6 A | 22 | 22 |  | 700 | [13 empty] | UL recognized | E180276 | JFHR2 | [6 empty] | www.woehner.com/de/products/31171.html | www.woehner.com/en/products/31171.html
31209 | Zylindr. Sicherungseinsatz 10 A | cylindr. fuse link 10 A | 22 | 22 |  | 700 | [13 empty] | UL recognized | E180276 | JFHR2 | [6 empty] | www.woehner.com/de/products/31205.html | www.woehner.com/en/products/31205.html
31210 | Zylindr. Sicherungseinsatz 12 A | cylindr. fuse link 12 A | 22 | 22 |  | 700 | [13 empty] | UL recognized | E180276 | JFHR2 | [6 empty] | www.woehner.com/de/products/31206.html | www.woehner.com/en/products/31206.html
31211 | Zylindr. Sicherungseinsatz 16 A | cylindr. fuse link 16 A | 22 | 22 |  | 700 | [13 empty] | UL recognized | E180276 | JFHR2 | [6 empty] | www.woehner.com/de/products/31207.html | www.woehner.com/en/products/31207.html
31212 | Zylindr. Sicherungseinsatz 20 A | cylindr. fuse link 20 A | 22 | 22 |  | 700 | [13 empty] | UL recognized | E180276 | JFHR2 | [6 empty] | www.woehner.com/de/products/31208.html | www.woehner.com/en/products/31208.html
31213 | Zylindr. Sicherungseinsatz 25 A | cylindr. fuse link 25 A | 22 | 22 |  | 700 | [13 empty] | UL recognized | E180276 | JFHR2 | [6 empty] | www.woehner.com/de/products/31209.html | www.woehner.com/en/products/31209.html
31214 | Zylindr. Sicherungseinsatz 30 A | cylindr. fuse link 30 A | 22 | 22 |  | 700 | [13 empty] | UL recognized | E180276 | JFHR2 | [6 empty] | www.woehner.com/de/products/31210.html | www.woehner.com/en/products/31210.html
31215 | Zylindr. Sicherungseinsatz 10 A | cylindr. fuse link 10 A | 22 | 22 |  | 700 | [13 empty] | UL recognized | E180276 | JFHR2 | [6 empty] | www.woehner.com/de/products/31211.html | www.woehner.com/en/products/31211.html
31216 | Zylindr. Sicherungseinsatz 16 A | cylindr. fuse link 16 A | 22 | 22 |  | 700 | [13 empty] | UL recognized | E180276 | JFHR2 | [6 empty] | www.woehner.com/de/products/31212.html | www.woehner.com/en/products/31212.html
31217 | Zylindr. Sicherungseinsatz 20 A | cylindr. fuse link 20 A | 22 | 22 |  | 700 | [13 empty] | UL recognized | E180276 | JFHR2 | [6 empty] | www.woehner.com/de/products/31213.html | www.woehner.com/en/products/31213.html
31219 | Zylindr. Sicherungseinsatz 32 A | cylindr. fuse link 32 A | 22 | 22 |  | 700 | [13 empty] | UL recognized | E180276 | JFHR2 | [6 empty] | www.woehner.com/de/products/31214.html | www.woehner.com/en/products/31214.html
31220 | Zylindr. Sicherungseinsatz 40 A | cylindr. fuse link 40 A | 22 | 22 |  | 700 | [13 empty] | UL recognized | E180276 | JFHR2 | [6 empty] | www.woehner.com/de/products/31215.html | www.woehner.com/en/products/31215.html
31221 | Zylindr. Sicherungseinsatz 50 A | cylindr. fuse link 50 A | 22 | 22 |  | 700 | [13 empty] | UL recognized | E180276 | JFHR2 | [6 empty] | www.woehner.com/de/products/31216.html | www.woehner.com/en/products/31216.html
31226 | Zylindr. Sicherungseinsatz 50 A | cylindr. fuse link 50 A | 22 | 22 |  | 700 | [13 empty] | UL recognized | E180276 | JFHR2 | [6 empty] | www.woehner.com/de/products/31217.html | www.woehner.com/en/products/31217.html
31227 | Zylindr. Sicherungseinsatz 63 A | cylindr. fuse link 63 A | 22 | 22 |  | 700 | [13 empty] | UL recognized | E180276 | JFHR2 | [6 empty] | www.woehner.com/de/products/31219.html | www.woehner.com/en/products/31219.html
31228 | Zylindr. Sicherungseinsatz 80 A | cylindr. fuse link 80 A | 22 | 22 |  | 700 | [13 empty] | UL recognized | E180276 | JFHR2 | [6 empty] | www.woehner.com/de/products/31220.html | www.woehner.com/en/products/31220.html
31229 | Zylindr. Sicherungseinsatz 100 A | cylindr. fuse link 100 A | 22 | 22 |  | 700 | [13 empty] | UL recognized | E180276 | JFHR2 | [6 empty] | www.woehner.com/de/products/31221.html | www.woehner.com/en/products/31221.html
31235 | Zylindr. Sicherungseinsatz 1 A, fast acting | cylindr. fuse link 1 A, fast acting | 22 | 32 |  | 600 |  | 1 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31226.html | www.woehner.com/en/products/31226.html
31236 | Zylindr. Sicherungseinsatz 2 A, fast acting | cylindr. fuse link 2 A, fast acting | 22 | 32 |  | 600 |  | 2 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31227.html | www.woehner.com/en/products/31227.html
31237 | Zylindr. Sicherungseinsatz 4 A, fast acting | cylindr. fuse link 4 A, fast acting | 22 | 32 |  | 600 |  | 4 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31228.html | www.woehner.com/en/products/31228.html
31238 | Zylindr. Sicherungseinsatz 6 A, fast acting | cylindr. fuse link 6 A, fast acting | 22 | 32 |  | 600 |  | 6 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31229.html | www.woehner.com/en/products/31229.html
31239 | Zylindr. Sicherungseinsatz 10 A, fast acting | cylindr. fuse link 10 A, fast acting | 22 | 32 |  | 600 |  | 10 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31235.html | www.woehner.com/en/products/31235.html
31240 | Zylindr. Sicherungseinsatz 15 A, fast acting | cylindr. fuse link 15 A, fast acting | 22 | 32 |  | 600 |  | 15 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31236.html | www.woehner.com/en/products/31236.html
31241 | Zylindr. Sicherungseinsatz 20 A, fast acting | cylindr. fuse link 20 A, fast acting | 22 | 32 |  | 600 |  | 20 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31237.html | www.woehner.com/en/products/31237.html
31242 | Zylindr. Sicherungseinsatz 25 A, fast acting | cylindr. fuse link 25 A, fast acting | 22 | 32 |  | 600 |  | 25 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31238.html | www.woehner.com/en/products/31238.html
31243 | Zylindr. Sicherungseinsatz 30 A, fast acting | cylindr. fuse link 30 A, fast acting | 22 | 32 |  | 600 |  | 30 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31239.html | www.woehner.com/en/products/31239.html
31244 | Zylindr. Sicherungseinsatz 1 A, time delay | cylindr. fuse link 1 A, time delay | 22 | 31 |  | 600 |  | 1 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31240.html | www.woehner.com/en/products/31240.html
31245 | Zylindr. Sicherungseinsatz 2 A, time delay | cylindr. fuse link 2 A, time delay | 22 | 31 |  | 600 |  | 2 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31241.html | www.woehner.com/en/products/31241.html
31246 | Zylindr. Sicherungseinsatz 4 A, time delay | cylindr. fuse link 4 A, time delay | 22 | 31 |  | 600 |  | 4 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31242.html | www.woehner.com/en/products/31242.html
31247 | Zylindr. Sicherungseinsatz 6 A, time delay | cylindr. fuse link 6 A, time delay | 22 | 31 |  | 600 |  | 6 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31243.html | www.woehner.com/en/products/31243.html
31248 | Zylindr. Sicherungseinsatz 10 A, time delay | cylindr. fuse link 10 A, time delay | 22 | 31 |  | 600 |  | 10 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31244.html | www.woehner.com/en/products/31244.html
31249 | Zylindr. Sicherungseinsatz 15 A, time delay | cylindr. fuse link 15 A, time delay | 22 | 31 |  | 600 |  | 15 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31245.html | www.woehner.com/en/products/31245.html
31250 | Zylindr. Sicherungseinsatz 20 A, time delay | cylindr. fuse link 20 A, time delay | 22 | 31 |  | 600 |  | 20 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31246.html | www.woehner.com/en/products/31246.html
31251 | Zylindr. Sicherungseinsatz 25 A, time delay | cylindr. fuse link 25 A, time delay | 22 | 31 |  | 600 |  | 25 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31247.html | www.woehner.com/en/products/31247.html
31252 | Zylindr. Sicherungseinsatz 30 A, time delay | cylindr. fuse link 30 A, time delay | 22 | 31 |  | 600 |  | 30 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31248.html | www.woehner.com/en/products/31248.html
31275 | Halter für zylindrische Sicherungen, für Halbleiterschutz | holder for cylindrical fuses, for semiconductor fuses | 17 | 06 | AES10x38 | 600 | 600 | 30 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31249.html | www.woehner.com/en/products/31249.html
31276 | Halter für zylindrische Sicherungen, für Halbleiterschutz | holder for cylindrical fuses, for semiconductor fuses | 17 | 06 | AES10x38 | 600 | 600 | 30 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31250.html | www.woehner.com/en/products/31250.html
31277 | Halter für zylindrische Sicherungen, für Halbleiterschutz | holder for cylindrical fuses, for semiconductor fuses | 17 | 06 | AES10x38 | 600 | 600 | 30 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31251.html | www.woehner.com/en/products/31251.html
31278 | Halter für zylindrische Sicherungen, für Halbleiterschutz | holder for cylindrical fuses, for semiconductor fuses | 17 | 09 | AES14x51 | 600 | 600 | 50 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31252.html | www.woehner.com/en/products/31252.html
31279 | Halter für zylindrische Sicherungen, für Halbleiterschutz | holder for cylindrical fuses, for semiconductor fuses | 17 | 09 | AES14x51 | 600 | 600 | 50 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31275.html | www.woehner.com/en/products/31275.html
31280 | Halter für zylindrische Sicherungen, für Halbleiterschutz | holder for cylindrical fuses, for semiconductor fuses | 17 | 09 | AES14x51 | 600 | 600 | 50 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31276.html | www.woehner.com/en/products/31276.html
31281 | Halter für zylindrische Sicherungen, für Halbleiterschutz | holder for cylindrical fuses, for semiconductor fuses | 17 | 12 | AES22x58 | 600 | 600 | 80 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31277.html | www.woehner.com/en/products/31277.html
31282 | Halter für zylindrische Sicherungen, für Halbleiterschutz | holder for cylindrical fuses, for semiconductor fuses | 17 | 12 | AES22x58 | 600 | 600 | 80 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31278.html | www.woehner.com/en/products/31278.html
31283 | Halter für zylindrische Sicherungen, für Halbleiterschutz | holder for cylindrical fuses, for semiconductor fuses | 17 | 12 | AES22x58 | 600 | 600 | 80 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31279.html | www.woehner.com/en/products/31279.html
31284 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 16 | 03 | AJC30 | 600 | 600 | 30 |  |  |  | 200 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31280.html | www.woehner.com/en/products/31280.html
31285 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 16 | 03 | AJC30 | 600 | 600 | 30 |  |  |  | 200 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31281.html | www.woehner.com/en/products/31281.html
31287 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 16 | 03 | AJC30 | 600 | 600 | 30 |  |  |  | 200 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31282.html | www.woehner.com/en/products/31282.html
31295 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 17 | 07 | AESCC | 600 | 600 | 30 |  |  |  | 200 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31283.html | www.woehner.com/en/products/31283.html
31296 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 17 | 07 | AESCC | 600 | 600 | 30 |  |  |  | 200 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31284.html | www.woehner.com/en/products/31284.html
31297 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 17 | 07 | AESCC | 600 | 600 | 30 |  |  |  | 200 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31285.html | www.woehner.com/en/products/31285.html
31298 | Halter für zylindrische Sicherungen, mit LED | holder for cylindrical fuses, with LED | 17 | 07 | AESCC | 600 | 600 | 30 |  |  |  | 200 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31287.html | www.woehner.com/en/products/31287.html
31299 | Halter für zylindrische Sicherungen, mit LED | holder for cylindrical fuses, with LED | 17 | 07 | AESCC | 600 | 600 | 30 |  |  |  | 200 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31295.html | www.woehner.com/en/products/31295.html
31300 | Halter für zylindrische Sicherungen, mit LED | holder for cylindrical fuses, with LED | 17 | 07 | AESCC | 600 | 600 | 30 |  |  |  | 200 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31296.html | www.woehner.com/en/products/31296.html
31323 | Sicherungseinsatz 10 A, fast acting (flink) | fuse link 10 A, fast acting | 22 | 34 | JKS | 600 |  | 10 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31297.html | www.woehner.com/en/products/31297.html
31324 | Sicherungseinsatz 15 A, fast acting (flink) | fuse link 15 A, fast acting | 22 | 34 | JKS | 600 |  | 15 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31298.html | www.woehner.com/en/products/31298.html
31325 | Sicherungseinsatz 20 A, fast acting (flink) | fuse link 20 A, fast acting | 22 | 34 | JKS | 600 |  | 20 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31299.html | www.woehner.com/en/products/31299.html
31326 | Sicherungseinsatz 25 A, fast acting (flink) | fuse link 25 A, fast acting | 22 | 34 | JKS | 600 |  | 25 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31300.html | www.woehner.com/en/products/31300.html
31327 | Sicherungseinsatz 30 A, fast acting (flink) | fuse link 30 A, fast acting | 22 | 34 | JKS | 600 |  | 30 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31323.html | www.woehner.com/en/products/31323.html
31333 | Sicherungseinsatz 1 A, time delay (träge) | fuse link 1 A, time delay | 22 | 33 | LPJ | 600 | 300 | 1 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31324.html | www.woehner.com/en/products/31324.html
31338 | Sicherungseinsatz 2 A, time delay (träge) | fuse link 2 A, time delay | 22 | 33 | LPJ | 600 | 300 | 2 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31325.html | www.woehner.com/en/products/31325.html
31342 | Sicherungseinsatz 3 A, time delay (träge) | fuse link 3 A, time delay | 22 | 33 | LPJ | 600 | 300 | 3 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31326.html | www.woehner.com/en/products/31326.html
31345 | Sicherungseinsatz 4 A, time delay (träge) | fuse link 4 A, time delay | 22 | 33 | LPJ | 600 | 300 | 4 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31327.html | www.woehner.com/en/products/31327.html
31349 | Sicherungseinsatz 6 A, time delay (träge) | fuse link 6 A, time delay | 22 | 33 | LPJ | 600 | 300 | 6 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31333.html | www.woehner.com/en/products/31333.html
31351 | Sicherungseinsatz 8 A, time delay (träge) | fuse link 8 A, time delay | 22 | 33 | LPJ | 600 | 300 | 8 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31338.html | www.woehner.com/en/products/31338.html
31353 | Sicherungseinsatz 10 A, time delay (träge) | fuse link 10 A, time delay | 22 | 33 | LPJ | 600 | 300 | 10 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31342.html | www.woehner.com/en/products/31342.html
31354 | Sicherungseinsatz 12 A, time delay (träge) | fuse link 12 A, time delay | 22 | 33 | LPJ | 600 | 300 | 12 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31345.html | www.woehner.com/en/products/31345.html
31355 | Sicherungseinsatz 15 A, time delay (träge) | fuse link 15 A, time delay | 22 | 33 | LPJ | 600 | 300 | 15 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31349.html | www.woehner.com/en/products/31349.html
31357 | Sicherungseinsatz 20 A, time delay (träge) | fuse link 20 A, time delay | 22 | 33 | LPJ | 600 | 300 | 20 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31351.html | www.woehner.com/en/products/31351.html
31358 | Sicherungseinsatz 25 A, time delay (träge) | fuse link 25 A, time delay | 22 | 33 | LPJ | 600 | 300 | 25 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31353.html | www.woehner.com/en/products/31353.html
31359 | Sicherungseinsatz 30 A, time delay (träge) | fuse link 30 A, time delay | 22 | 33 | LPJ | 600 | 300 | 30 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31354.html | www.woehner.com/en/products/31354.html
31360 | Sicherungseinsatz 35 A, time delay (träge) | fuse link 35 A, time delay | 22 | 33 | LPJ | 600 | 300 | 35 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31355.html | www.woehner.com/en/products/31355.html
31361 | Sicherungseinsatz 40 A, time delay (träge) | fuse link 40 A, time delay | 22 | 33 | LPJ | 600 | 300 | 40 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31357.html | www.woehner.com/en/products/31357.html
31362 | Sicherungseinsatz 45 A, time delay (träge) | fuse link 45 A, time delay | 22 | 33 | LPJ | 600 | 300 | 45 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31358.html | www.woehner.com/en/products/31358.html
31363 | Sicherungseinsatz 50 A, time delay (träge) | fuse link 50 A, time delay | 22 | 33 | LPJ | 600 |  | 50 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31359.html | www.woehner.com/en/products/31359.html
31364 | Sicherungseinsatz 60 A, time delay (träge) | fuse link 60 A, time delay | 22 | 33 | LPJ | 600 |  | 60 |  |  |  | 200 | [5 empty] | Yes |  | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31360.html | www.woehner.com/en/products/31360.html
31394 | Zylindr. Sicherungseinsatz 0,5 A, time delay | cylindr. fuse link 0,5 A, time delay | 22 | 31 |  | 600 |  | 0,5 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31361.html | www.woehner.com/en/products/31361.html
31395 | Zylindr. Sicherungseinsatz 1,5 A, time delay | cylindr. fuse link 1,5 A, time delay | 22 | 31 |  | 600 |  | 1,5 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31362.html | www.woehner.com/en/products/31362.html
31396 | Zylindr. Sicherungseinsatz 2,5 A, time delay | cylindr. fuse link 2,5 A, time delay | 22 | 31 |  | 600 |  | 2,5 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31363.html | www.woehner.com/en/products/31363.html
31397 | Zylindr. Sicherungseinsatz 3 A, time delay | cylindr. fuse link 3 A, time delay | 22 | 31 |  | 600 |  | 3 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31364.html | www.woehner.com/en/products/31364.html
31398 | Zylindr. Sicherungseinsatz 5 A, time delay | cylindr. fuse link 5 A, time delay | 22 | 31 |  | 600 |  | 5 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31394.html | www.woehner.com/en/products/31394.html
31399 | Zylindr. Sicherungseinsatz 8 A, time delay | cylindr. fuse link 8 A, time delay | 22 | 31 |  | 600 |  | 8 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31395.html | www.woehner.com/en/products/31395.html
31400 | Zylindr. Sicherungseinsatz 12 A, time delay | cylindr. fuse link 12 A, time delay | 22 | 31 |  | 600 |  | 12 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31396.html | www.woehner.com/en/products/31396.html
31401 | Zylindr. Sicherungseinsatz 0,5 A, fast acting | cylindr. fuse link 0,5 A, fast acting | 22 | 32 |  | 600 |  | 0,5 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31397.html | www.woehner.com/en/products/31397.html
31404 | Zylindr. Sicherungseinsatz 3 A, fast acting | cylindr. fuse link 3 A, fast acting | 22 | 32 |  | 600 |  | 3 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31398.html | www.woehner.com/en/products/31398.html
31405 | Zylindr. Sicherungseinsatz 5 A, fast acting | cylindr. fuse link 5 A, fast acting | 22 | 32 |  | 600 |  | 5 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31399.html | www.woehner.com/en/products/31399.html
31406 | Zylindr. Sicherungseinsatz 8 A, fast acting | cylindr. fuse link 8 A, fast acting | 22 | 32 |  | 600 |  | 8 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31400.html | www.woehner.com/en/products/31400.html
31407 | Zylindr. Sicherungseinsatz 12 A, fast acting | cylindr. fuse link 12 A, fast acting | 22 | 32 |  | 600 |  | 12 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31401.html | www.woehner.com/en/products/31401.html
31511 | Sicherungseinsatz 35 A, fast acting (flink) | fuse link 35 A, fast acting | 22 | 34 | JKS | 600 |  | 35 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31404.html | www.woehner.com/en/products/31404.html
31512 | Sicherungseinsatz 40 A, fast acting (flink) | fuse link 40 A, fast acting | 22 | 34 | JKS | 600 |  | 40 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31405.html | www.woehner.com/en/products/31405.html
31514 | Sicherungseinsatz 50 A, fast acting (flink) | fuse link 50 A, fast acting | 22 | 34 | JKS | 600 |  | 50 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31406.html | www.woehner.com/en/products/31406.html
31515 | Sicherungseinsatz 60 A, fast acting (flink) | fuse link 60 A, fast acting | 22 | 34 | JKS | 600 |  | 60 |  |  |  | 200 | [7 empty] | UL listed | E4273 | JDDZ |  |  |  |  | 53787 | 1422-02 | www.woehner.com/de/products/31407.html | www.woehner.com/en/products/31407.html
31548 | Kammschiene 1-polig, Steg, Teilung 18 mm | comb-type busbar, 1-pole, bridge type, pitch 18 mm | 06 | 95 | CTB25-118 | 600 | 600 | 100 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/31511.html | www.woehner.com/en/products/31511.html
31549 | Kammschiene 3-polig, Steg, Teilung 18 mm | comb-type busbar, 3-pole, bridge type, pitch 18 mm | 06 | 95 | CTB25-318 | 600 |  | 100 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/31512.html | www.woehner.com/en/products/31512.html
31550 | Anschlussklemme, frontaler Anschluss | connection terminal, front connection | 07 | 26 | CTB-T35 | 600 | 600 | 115 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/31514.html | www.woehner.com/en/products/31514.html
31552 | Endkappe | end cap | 06 | 30 | CTB-C3 | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/31515.html | www.woehner.com/en/products/31515.html
31555 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 17 | 18 | AES10x85 |  | 1500 | 30 |  |  |  | 15 | [7 empty] | UL listed | E342576 | IZMR | [6 empty] | www.woehner.com/de/products/31548.html | www.woehner.com/en/products/31548.html
31561 | Kammschiene 2-polig, Steg, Teilung 18 mm | comb-type busbar, 2-pole, bridge type, pitch 18 mm | 06 | 95 | CTB25-318 | 600 | 600 | 100 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/31549.html | www.woehner.com/en/products/31549.html
31570 | Reiter-Sicherungshalter 1000 V | busbar mounted fuse holder 1000 V | 01 | 46 | AEL10x38/PV-30 |  | 1000 | 30 |  |  |  | 33 | [7 empty] | UL recognized | E230163 | IZLT2 | IZLT8 |  | IZMR2 |  |  |  | www.woehner.com/de/products/31550.html | www.woehner.com/en/products/31550.html
31571 | Reiter-Sicherungshalter 1000 V, mit LED | bus-mouning fuse holder 1000 V, with LED | 01 | 46 | AEL10x38/PV-30 |  | 1000 | 30 |  |  |  | 33 | [7 empty] | UL recognized | E230163 | IZLT2 | IZLT8 |  | IZMR2 |  |  |  | www.woehner.com/de/products/31552.html | www.woehner.com/en/products/31552.html
31572 | Reiter-Sicherungshalter 1000 V | busbar mounted fuse holder 1000 V | 01 | 46 | AEL10x38/PV-20 |  | 1000 | 30 |  |  |  | 33 | [7 empty] | UL recognized | E230163 | IZLT2 | IZLT8 |  | IZMR2 |  |  |  | www.woehner.com/de/products/31555.html | www.woehner.com/en/products/31555.html
31920 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 16 | 06 | AJC60 | 600 | 600 | 60 |  |  |  | 200 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31561.html | www.woehner.com/en/products/31561.html
31921 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 16 | 06 | AJC60 | 600 | 600 | 60 |  |  |  | 200 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31570.html | www.woehner.com/en/products/31570.html
31922 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 16 | 06 | AJC60 | 600 | 600 | 60 |  |  |  | 200 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31571.html | www.woehner.com/en/products/31571.html
31923 | Halter für zylindrische Sicherungen, mit LED | holder for cylindrical fuses, with LED | 16 | 06 | AJC60 | 600 | 600 | 60 |  |  |  | 200 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31572.html | www.woehner.com/en/products/31572.html
31924 | Halter für zylindrische Sicherungen, mit LED | holder for cylindrical fuses, with LED | 16 | 06 | AJC60 | 600 | 600 | 60 |  |  |  | 200 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31920.html | www.woehner.com/en/products/31920.html
31925 | Halter für zylindrische Sicherungen, mit LED | holder for cylindrical fuses, with LED | 16 | 06 | AJC60 | 600 | 600 | 60 |  |  |  | 200 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31921.html | www.woehner.com/en/products/31921.html
31929 | Halter für zylindrische Sicherungen, mit LED | holder for cylindrical fuses, with LED | 17 | 07 | AESCC | 72 | 72 | 30 |  |  |  | 200 | [5 empty] | No | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31922.html | www.woehner.com/en/products/31922.html
31930 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 17 | 06 | AES10x38 | 72 | 72 | 30 |  |  |  | 100 | [7 empty] | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31923.html | www.woehner.com/en/products/31923.html
31932 | Halter für zylindrische Sicherungen, mit LED | holder for cylindrical fuses, with LED | 16 | 03 | AJC30 | 600 | 600 | 30 |  |  |  | 200 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31924.html | www.woehner.com/en/products/31924.html
31933 | Halter für zylindrische Sicherungen, mit LED | holder for cylindrical fuses, with LED | 16 | 03 | AJC30 | 600 | 600 | 30 |  |  |  | 200 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31925.html | www.woehner.com/en/products/31925.html
31934 | Halter für zylindrische Sicherungen, mit LED | holder for cylindrical fuses, with LED | 16 | 03 | AJC30 | 600 | 600 | 30 |  |  |  | 200 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31929.html | www.woehner.com/en/products/31929.html
31940 | Halter für zylindrische Sicherungen, mit Meldeschalter | holder for cylindrical fuses, with pilot switch | 17 | 09 | AES14x51 | 600 | 600 | 50 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31930.html | www.woehner.com/en/products/31930.html
31941 | Halter für zylindrische Sicherungen, mit Meldeschalter | holder for cylindrical fuses, with pilot switch | 17 | 09 | AES14x51 | 600 | 600 | 50 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31932.html | www.woehner.com/en/products/31932.html
31942 | Halter für zylindrische Sicherungen, mit Meldeschalter | holder for cylindrical fuses, with pilot switch | 17 | 12 | AES22x58 | 600 | 600 | 80 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31933.html | www.woehner.com/en/products/31933.html
31943 | Halter für zylindrische Sicherungen, mit Meldeschalter | holder for cylindrical fuses, with pilot switch | 17 | 12 | AES22x58 | 600 | 600 | 80 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31934.html | www.woehner.com/en/products/31934.html
31954 | Reiter-Sicherungshalter | busbar mounted fuse holder | 01 | 46 | AEL10x38 | 600 | 600 | 30 |  |  |  | 50 | [5 empty] | Yes | Yes | UL recognized | E230163 | IZLT2 | IZLT8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/31940.html | www.woehner.com/en/products/31940.html
31955 | Reiter-Sicherungshalter, mit LED | busbar mounted fuse holder, with LED | 01 | 46 | AEL10x38 | 600 | 600 | 30 |  |  |  | 50 | [5 empty] | Yes | Yes | UL recognized | E230163 | IZLT2 | IZLT8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/31941.html | www.woehner.com/en/products/31941.html
31957 | Halter für zylindrische Sicherungen, mit Meldeschalter | holder for cylindrical fuses, with pilot switch | 17 | 12 | AES22x58 | 600 | 600 | 80 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31942.html | www.woehner.com/en/products/31942.html
31958 | Reiter-Sicherungshalter | busbar mounted fuse holder | 01 | 47 | AELCC | 600 |  | 30 | [9 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/31943.html | www.woehner.com/en/products/31943.html
31959 | Reiter-Sicherungshalter, mit LED | busbar mounted fuse holder, with LED | 01 | 47 | AELCC | 600 |  | 30 | [9 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/31954.html | www.woehner.com/en/products/31954.html
31968 | Reiter-Sicherungshalter Class J, Anschluss unten | busbar mounted fuse holder Class J, connection bottom | 16 | 21 | EEC6032-L + AJC30 | 600 | 600 | 30 |  |  |  | 100 | [7 empty] | UL listed | E230163 | IZLT | IZLT7 | E123577 | NMTR |  | 110285 | 3211-37 | www.woehner.com/de/products/31955.html | www.woehner.com/en/products/31955.html
31970 | Reiter-Sicherungshalter Class J, Anschluss unten | busbar mounted fuse holder Class J, connection bottom | 16 | 24 | EEC6080-L + AJC60 | 600 | 600 | 60 |  |  |  | 100 | [7 empty] | UL listed | E230163 | IZLT | IZLT7 | E123577 | NMTR |  | 110285 | 3211-37 | www.woehner.com/de/products/31957.html | www.woehner.com/en/products/31957.html
31971 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 17 | 06 | AES10x38/PV |  | 1000 | 30 | [6 empty] | 33 | fuse link IZLT 10x38 30 A / 1000 V DC |  | Yes | Yes | UL listed | E342576 | IZMR |  |  |  |  | 110285 | 6225-30 | www.woehner.com/de/products/31958.html | www.woehner.com/en/products/31958.html
31972 | Halter für zylindrische Sicherungen, mit Meldeschalter | holder for cylindrical fuses, with pilot switch | 17 | 09 | AES14x51 | 600 | 600 | 50 |  |  |  | 100 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 6225-01 | www.woehner.com/de/products/31959.html | www.woehner.com/en/products/31959.html
31973 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 17 | 06 | AES10x38/PV |  | 1000 | 30 | [6 empty] | 33 | fuse link IZLT 10x38 30 A / 1000 V DC |  | Yes | Yes | UL listed | E342576 | IZMR |  |  |  |  | 110285 | 6225-30 | www.woehner.com/de/products/31968.html | www.woehner.com/en/products/31968.html
31974 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 17 | 06 | AES10x38/PV |  | 1000 | 30 | [6 empty] | 33 | fuse link IZLT 10x38 30 A / 1000 V DC |  | Yes | Yes | UL listed | E342576 | IZMR |  |  |  |  | 110285 | 6225-30 | www.woehner.com/de/products/31970.html | www.woehner.com/en/products/31970.html
32017 | Sammelschienenadapter 250 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 250 A, 3-pole, aligned to switchgear | 05 | 36 | EPC60250-L | 600 |  | 250 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/31971.html | www.woehner.com/en/products/31971.html
32018 | Sammelschienenadapter 160 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 160 A, 3-pole, aligned to switchgear | 05 | 30 | EPC60160-L | 600 |  | 160 | [8 empty] | 35kA @ circuit breaker DIVQ/7 125A, 480Vac | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/31972.html | www.woehner.com/en/products/31972.html
32020 | Sammelschienenadapter 160 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 160 A, 3-pole, aligned to switchgear | 05 | 30 | EPC60160 | 600 |  | 160 | [8 empty] | 35kA @ circuit breaker DIVQ/7 125A, 480Vac | Yes |  | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/31973.html | www.woehner.com/en/products/31973.html
32023 | Sammelschienenadapter 250 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 250 A, 3-pole, aligned to switchgear | 05 | 36 | 60250.1-L | 600 |  | 250 | [6 empty] | 65 | 65kA @ circuit breaker DIVQ/7 250A, 480Vac | 65kA @ circuit breaker DIVQ/7 250A, 480Vac | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/31974.html | www.woehner.com/en/products/31974.html
32023 | Sammelschienenadapter 250 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 250 A, 3-pole, aligned to switchgear | 05 | 36 | 60250.1-L | 600 |  | 250 | [6 empty] | 65 | 65kA @ circuit breaker DIVQ/7 250A, 480Vac | 25kA @ circuit breaker DIVQ/7 250A, 600Vac | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32017.html | www.woehner.com/en/products/32017.html
32028 | Sammelschienenadapter 160 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 160 A, 3-pole, aligned to switchgear | 05 | 30 | EPC60160-L | 600 |  | 125 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32018.html | www.woehner.com/en/products/32018.html
32029 | Sammelschienenadapter 80 A, angepasst auf Schaltgeräte | busbar adapter 80 A, aligned to switchgear | 05 | 27 | EEC60100-L | 600 |  | 80 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32020.html | www.woehner.com/en/products/32020.html
32030 | Sammelschienenadapter 160 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 160 A, 3-pole, aligned to switchgear | 05 | 30 | EPC60160-L | 600 |  | 125 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32023.html | www.woehner.com/en/products/32023.html
32031 | Sammelschienenadapter 590 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 590 A, 3-pole, aligned to switchgear | 05 | 42 | EPC60630-L | 600 |  | 630 |  |  |  |  | 30 |  |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32023.html | www.woehner.com/en/products/32023.html
32033 | Sammelschienenadapter 590 A, 4-polig, angepasst auf Schaltgeräte | busbar adapter 590 A, 4-pole, aligned to switchgear | 05 | 42 | EPC60630-L | 600 |  | 630 |  |  |  |  | 30 |  |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR8 | [5 empty] | www.woehner.com/de/products/32028.html | www.woehner.com/en/products/32028.html
32064 | Sammelschienenadapter 650 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 650 A, 3-pole, aligned to switchgear | 05 | 42 | EPC60800-L | 600 |  | 640 | [6 empty] | 65 | 65 kA / Allen-Bradley 140G-M @ 480V | 65 kA / Allen-Bradley 140G-M @ 480V | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32029.html | www.woehner.com/en/products/32029.html
32064 | Sammelschienenadapter 650 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 650 A, 3-pole, aligned to switchgear | 05 | 42 | EPC60800-L | 600 |  | 640 | [6 empty] | 65 | 65 kA / Allen-Bradley 140G-M @ 480V | 42 kA / Allen-Bradley 140G-M @ 600 V | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32030.html | www.woehner.com/en/products/32030.html
32067 | Sammelschienenadapter 250 A, 4-polig, angepasst auf Schaltgeräte | busbar adapter 250 A, 4-pole, aligned to switchgear | 05 | 36 | EPC60250-L | 600 |  | 250 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32031.html | www.woehner.com/en/products/32031.html
32137 | Sammelschienenadapter 250 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 250 A, 3-pole, aligned to switchgear | 05 | 36 | 60250.1-L | 600 |  | 250 | [6 empty] | 65 | 65kA @ 140U J-Frame 480V | 65kA @ 140U J-Frame 480V | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32033.html | www.woehner.com/en/products/32033.html
32137 | Sammelschienenadapter 250 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 250 A, 3-pole, aligned to switchgear | 05 | 36 | 60250.1-L | 600 |  | 250 | [6 empty] | 65 | 65kA @ 140U J-Frame 480V | 25kA @ 140U J-Frame 600V | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32064.html | www.woehner.com/en/products/32064.html
32138 | Sammelschienenadapter 600 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 600 A, 3-pole, aligned to switchgear | 05 | 42 | 60630.1-L | 600 |  | 630 | [6 empty] | 65 | 65kA @ 140-U L-Frame 480V | 35kA @ 140-U L-Frame 600V | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32064.html | www.woehner.com/en/products/32064.html
32138 | Sammelschienenadapter 600 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 600 A, 3-pole, aligned to switchgear | 05 | 42 | 60630.1-L | 600 |  | 630 | [6 empty] | 65 | 65kA @ 140-U L-Frame 480V | 65kA @ 140-U L-Frame 480V | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32067.html | www.woehner.com/en/products/32067.html
32140 | Sammelschienenadapter 250 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 250 A, 3-pole, aligned to switchgear | 05 | 36 | 60250.1-L | 600 |  | 250 | [6 empty] | 65 | 65kA @NZMH2 480V | 50kA @NZMH2 600V | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32137.html | www.woehner.com/en/products/32137.html
32140 | Sammelschienenadapter 250 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 250 A, 3-pole, aligned to switchgear | 05 | 36 | 60250.1-L | 600 |  | 250 | [6 empty] | 65 | 65kA @NZMH2 480V | 65kA @NZMH2 480V | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32137.html | www.woehner.com/en/products/32137.html
32146 | PE/N-Adaptermodul | module PE/N | 05 | 43 | 680.1 | [14 empty] | UL recognized | E123577 | NMTR2 | NMTR8 | [5 empty] | www.woehner.com/de/products/32138.html | www.woehner.com/en/products/32138.html
32153 | Adapter 80 A, 1 Tragschiene | adapter 80 A, 1 mounting rail | 05 | 27 | 6080 | 600 |  | 80 | [9 empty] | Yes |  | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32138.html | www.woehner.com/en/products/32138.html
32156 | Sammelschienenadapter 250 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 250 A, 3-pole, aligned to switchgear | 05 | 36 | 60250.1-L | 600 |  | 250 |  |  |  |  | 30 |  | 65 | 65 kA / NSX250 @ 480 V | 65 kA / NSX250 @ 480 V | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32140.html | www.woehner.com/en/products/32140.html
32156 | Sammelschienenadapter 250 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 250 A, 3-pole, aligned to switchgear | 05 | 36 | 60250.1-L | 600 |  | 250 |  |  |  |  | 30 |  | 65 | 65 kA / NSX250 @ 480 V | 25k A / NSX250 @ 600 V | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32140.html | www.woehner.com/en/products/32140.html
32157 | Sammelschienenadapter 570 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 570 A, 3-pole, aligned to switchgear | 05 | 42 | 60630.1-L | 600 |  | 630 | [6 empty] | 65 | 65 kA / NS400 @ 480 V | 25 kA / NS630 @ 600 V | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32146.html | www.woehner.com/en/products/32146.html
32157 | Sammelschienenadapter 570 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 570 A, 3-pole, aligned to switchgear | 05 | 42 | 60630.1-L | 600 |  | 630 | [6 empty] | 65 | 65 kA / NS400 @ 480 V | 50 kA / NS630 @ 480 V | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32153.html | www.woehner.com/en/products/32153.html
32157 | Sammelschienenadapter 570 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 570 A, 3-pole, aligned to switchgear | 05 | 42 | 60630.1-L | 600 |  | 630 | [6 empty] | 65 | 65 kA / NS400 @ 480 V | 65 kA / NS400 @ 480 V | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32156.html | www.woehner.com/en/products/32156.html
32157 | Sammelschienenadapter 570 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 570 A, 3-pole, aligned to switchgear | 05 | 42 | 60630.1-L | 600 |  | 630 | [6 empty] | 65 | 65 kA / NS400 @ 480 V | 35 kA / NS400 @ 600 V | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32156.html | www.woehner.com/en/products/32156.html
32168 | Sammelschienenadapter 250 A | busbar adapter 250 A | 05 | 36 | 60250 | 600 |  | 250 | [11 empty] | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32157.html | www.woehner.com/en/products/32157.html
32170 | Sammelschienenadapter 550 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 550 A, 3-pole, aligned to switchgear | 05 | 42 | 60630.1-L | 600 |  | 630 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32157.html | www.woehner.com/en/products/32157.html
32214 | Sammelschienenadapter 200 A | busbar adapter 200 A | 05 | 36 | 60200 | 600 |  | 200 | [11 empty] | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32157.html | www.woehner.com/en/products/32157.html
32215 | Sammelschienenadapter 200 A | busbar adapter 200 A | 05 | 36 | 60200 | 600 |  | 200 | [11 empty] | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32157.html | www.woehner.com/en/products/32157.html
32216 | Sammelschienenadapter 250 A | busbar adapter 250 A | 05 | 36 | 60250 | 600 |  | 250 | [11 empty] | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32168.html | www.woehner.com/en/products/32168.html
32226 | Sammelschienenadapter 100 A / 400 V | adapter 100 A / 400 V | 05 | 28 | 4610.1 | 400 |  | 100 | [11 empty] | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32170.html | www.woehner.com/en/products/32170.html
32300 | Adapter 16 A, mit CrossLink®-Schnittstelle | adapter 16 A, with CrossLink® interface | 05 | 19 | EQ18-AA | 600 |  | 16 |  |  |  |  | 6 | 3 cycles (without OPD) @ 600 V AC | 65 | any NKJH/7 16 A @ 480 V AC (3-pole) or any NKJH/7 16 A @ 277 V AC (1-pole) | 14 kA / DIVQ7 16 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32192.html | www.woehner.com/en/products/32192.html
32300 | Adapter 16 A, mit CrossLink®-Schnittstelle | adapter 16 A, with CrossLink® interface | 05 | 19 | EQ18-AA | 600 |  | 16 |  |  |  |  | 6 | 3 cycles (without OPD) @ 600 V AC | 65 | any NKJH/7 16 A @ 480 V AC (3-pole) or any NKJH/7 16 A @ 277 V AC (1-pole) | 50 kA / Class CC 20 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32214.html | www.woehner.com/en/products/32214.html
32300 | Adapter 16 A, mit CrossLink®-Schnittstelle | adapter 16 A, with CrossLink® interface | 05 | 19 | EQ18-AA | 600 |  | 16 |  |  |  |  | 6 | 3 cycles (without OPD) @ 600 V AC | 65 | any NKJH/7 16 A @ 480 V AC (3-pole) or any NKJH/7 16 A @ 277 V AC (1-pole) | 65 kA / NKJH/7 16 A @ 480 V AC (3-pole) or NKJH/7 16 A @ 277 V AC (1-pole) | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32215.html | www.woehner.com/en/products/32215.html
32301 | Adapter 16 A, mit CrossLink®-Schnittstelle | adapter 16 A, with CrossLink® interface | 05 | 19 | EQ18-AA | 600 |  | 16 |  |  |  |  | 6 | 3 cycles (without OPD) @ 600 V AC | 65 | any NKJH/7 16 A @ 480 V AC (3-pole) or any NKJH/7 16 A @ 277 V AC (1-pole) | 14 kA / DIVQ7 16 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32216.html | www.woehner.com/en/products/32216.html
32301 | Adapter 16 A, mit CrossLink®-Schnittstelle | adapter 16 A, with CrossLink® interface | 05 | 19 | EQ18-AA | 600 |  | 16 |  |  |  |  | 6 | 3 cycles (without OPD) @ 600 V AC | 65 | any NKJH/7 16 A @ 480 V AC (3-pole) or any NKJH/7 16 A @ 277 V AC (1-pole) | 50 kA / Class CC 20 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32226.html | www.woehner.com/en/products/32226.html
32301 | Adapter 16 A, mit CrossLink®-Schnittstelle | adapter 16 A, with CrossLink® interface | 05 | 19 | EQ18-AA | 600 |  | 16 |  |  |  |  | 6 | 3 cycles (without OPD) @ 600 V AC | 65 | any NKJH/7 16 A @ 480 V AC (3-pole) or any NKJH/7 16 A @ 277 V AC (1-pole) | 65 kA / NKJH/7 16 A @ 480 V AC (3-pole) or NKJH/7 16 A @ 277 V AC (1-pole) | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32294.html | www.woehner.com/en/products/32294.html
32302 | Adapter 16 A, mit CrossLink®-Schnittstelle | adapter 16 A, with CrossLink® interface | 05 | 19 | EQ18-AA | 600 |  | 16 |  |  |  |  | 6 | 3 cycles (without OPD) @ 600 V AC | 50 | any NKJH/7 16 A @ 480 V AC (3-pole) or any NKJH/7 16 A @ 277 V AC (1-pole) | 14 kA / DIVQ7 16 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32300.html | www.woehner.com/en/products/32300.html
32302 | Adapter 16 A, mit CrossLink®-Schnittstelle | adapter 16 A, with CrossLink® interface | 05 | 19 | EQ18-AA | 600 |  | 16 |  |  |  |  | 6 | 3 cycles (without OPD) @ 600 V AC | 50 | any NKJH/7 16 A @ 480 V AC (3-pole) or any NKJH/7 16 A @ 277 V AC (1-pole) | 50 kA / Class CC 20 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32301.html | www.woehner.com/en/products/32301.html
32302 | Adapter 16 A, mit CrossLink®-Schnittstelle | adapter 16 A, with CrossLink® interface | 05 | 19 | EQ18-AA | 600 |  | 16 |  |  |  |  | 6 | 3 cycles (without OPD) @ 600 V AC | 50 | any NKJH/7 16 A @ 480 V AC (3-pole) or any NKJH/7 16 A @ 277 V AC (1-pole) | 65 kA / NKJH/7 16 A @ 480 V AC (3-pole) or NKJH/7 16 A @ 277 V AC (1-pole) | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32302.html | www.woehner.com/en/products/32302.html
32307 | Adapter 63 A, mit CrossLink®-Schnittstelle | adapter 63 A, with CrossLink® interface | 05 | 20 | EQ18-AD | 600 |  | 63 |  |  |  |  | 6 | 3 cycles (without OPD) @ 600 V AC | 65 | any NKJH/7 63 A @ 480 V AC (3-pole) or any NKJH/7 63 A @ 277 V AC (1-pole) | 65 kA / NKJH/7 63 A @ 480 V AC (3-pole) or NKJH/7 63 A @ 277 V AC (1-pole) | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32307.html | www.woehner.com/en/products/32307.html
32307 | Adapter 63 A, mit CrossLink®-Schnittstelle | adapter 63 A, with CrossLink® interface | 05 | 20 | EQ18-AD | 600 |  | 63 |  |  |  |  | 6 | 3 cycles (without OPD) @ 600 V AC | 65 | any NKJH/7 63 A @ 480 V AC (3-pole) or any NKJH/7 63 A @ 277 V AC (1-pole) | 10 kA / DIVQ7 63 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32308.html | www.woehner.com/en/products/32308.html
32308 | Adapter 63 A, mit CrossLink®-Schnittstelle | adapter 63 A, with CrossLink® interface | 05 | 20 | EQ18-AD | 600 |  | 63 |  |  |  |  | 6 | 3 cycles (without OPD) @ 600 V AC | 65 | any NKJH/7 63 A @ 480 V AC (3-pole) or any NKJH/7 63 A @ 277 V AC (1-pole) | 65 kA / NKJH/7 63 A @ 480 V AC (3-pole) or NKJH/7 63 A @ 277 V AC (1-pole) | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32309.html | www.woehner.com/en/products/32309.html
32308 | Adapter 63 A, mit CrossLink®-Schnittstelle | adapter 63 A, with CrossLink® interface | 05 | 20 | EQ18-AD | 600 |  | 63 |  |  |  |  | 6 | 3 cycles (without OPD) @ 600 V AC | 65 | any NKJH/7 63 A @ 480 V AC (3-pole) or any NKJH/7 63 A @ 277 V AC (1-pole) | 10 kA / DIVQ7 63 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32400.html | www.woehner.com/en/products/32400.html
32309 | Adapter 63 A, mit CrossLink®-Schnittstelle | adapter 63 A, with CrossLink® interface | 05 | 20 | EQ18-AD | 600 |  | 63 |  |  |  |  | 6 | 3 cycles (without OPD) @ 600 V AC | 65 | any NKJH/7 63 A @ 480 V AC (3-pole) or any NKJH/7 63 A @ 277 V AC (1-pole) | 10 kA / DIVQ7 63 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32401.html | www.woehner.com/en/products/32401.html
32309 | Adapter 63 A, mit CrossLink®-Schnittstelle | adapter 63 A, with CrossLink® interface | 05 | 20 | EQ18-AD | 600 |  | 63 |  |  |  |  | 6 | 3 cycles (without OPD) @ 600 V AC | 65 | any NKJH/7 63 A @ 480 V AC (3-pole) or any NKJH/7 63 A @ 277 V AC (1-pole) | 65 kA / NKJH/7 63 A @ 480 V AC (3-pole) or NKJH/7 63 A @ 277 V AC (1-pole) | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32402.html | www.woehner.com/en/products/32402.html
32311 | Geräteträger mit CrossLink®-Schnittstelle | component support with CrossLink® interface | 05 | 17 | EQ18-A0 | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32404.html | www.woehner.com/en/products/32404.html
32400 | Sammelschienenadapter 25 A, mit CrossLink®-Schnittstelle | busbar adapter 25 A, with CrossLink® interface | 05 | 22 | EMC6025-L | 600 |  | 25 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32408.html | www.woehner.com/en/products/32408.html
32401 | Sammelschienenadapter 16 A, mit CrossLink®-Schnittstelle, angepasst auf Schaltgeräte | busbar adapter 16 A, with CrossLink® interface, aligned to switchgear | 05 | 22 | EMC6025-L | 600 |  | 12 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32412.html | www.woehner.com/en/products/32412.html
32402 | Sammelschienenadapter 25 A, mit CrossLink®-Schnittstelle | busbar adapter 25 A, with CrossLink® interface | 05 | 22 | EMC6025-L | 600 |  | 25 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32416.html | www.woehner.com/en/products/32416.html
32404 | Sammelschienenadapter 32 A, mit CrossLink®-Schnittstelle | busbar adapter 32 A, with CrossLink® interface | 05 | 22 | EMC6032-L | 600 |  | 30 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32420.html | www.woehner.com/en/products/32420.html
32408 | Sammelschienenadapter 32 A, mit CrossLink®-Schnittstelle | busbar adapter 32 A, with CrossLink® interface | 05 | 22 | EMC6032-L | 600 |  | 30 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32421.html | www.woehner.com/en/products/32421.html
32412 | Sammelschienenadapter 45 A, mit CrossLink®-Schnittstelle | busbar adapter 45 A, with CrossLink® interface | 05 | 22 | EMC6045-L | 600 |  | 45 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32425.html | www.woehner.com/en/products/32425.html
32416 | Sammelschienenadapter 45 A, mit CrossLink®-Schnittstelle | busbar adapter 45 A, with CrossLink® interface | 05 | 22 | EMC6045-L | 600 |  | 45 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32426.html | www.woehner.com/en/products/32426.html
32420 | Sammelschienengeräteträger, mit CrossLink®-Schnittstelle | busbar component support, with CrossLink® interface | 05 | 17 | EMC6000-L | 600 | [11 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32427.html | www.woehner.com/en/products/32427.html
32421 | Sammelschienengeräteträger, mit CrossLink®-Schnittstelle | busbar component support, with CrossLink® interface | 05 | 17 | EMC6000-L | 600 | [11 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32427.html | www.woehner.com/en/products/32427.html
32425 | Sammelschienengeräteträger, mit CrossLink®-Schnittstelle | busbar component support, with CrossLink® interface | 05 | 17 | EMC6000-L | 600 | [11 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32427.html | www.woehner.com/en/products/32427.html
32426 | Sammelschienengeräteträger, mit CrossLink®-Schnittstelle | busbar component support, with CrossLink® interface | 05 | 17 | EMC6000-L | 600 | [11 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32427.html | www.woehner.com/en/products/32427.html
32427 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65 kA / LUB32 25 A @ 480 V AC | 50 kA / LUB32 32A @ 480V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32428.html | www.woehner.com/en/products/32428.html
32427 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65 kA / LUB32 25 A @ 480 V AC | 65 kA / LUB32 16 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32428.html | www.woehner.com/en/products/32428.html
32427 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65 kA / LUB32 25 A @ 480 V AC | 65 kA / LUB32 25 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32428.html | www.woehner.com/en/products/32428.html
32427 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65 kA / LUB32 25 A @ 480 V AC | 30 kA / LUB12/32 12,5 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32428.html | www.woehner.com/en/products/32428.html
32428 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65 kA / LUB32 25 A @ 480 V AC | 50 kA / LUB32 32A @ 480V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32429.html | www.woehner.com/en/products/32429.html
32428 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65 kA / LUB32 25 A @ 480 V AC | 65 kA / LUB32 16 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32430.html | www.woehner.com/en/products/32430.html
32428 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65 kA / LUB32 25 A @ 480 V AC | 65 kA / LUB32 25 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32430.html | www.woehner.com/en/products/32430.html
32428 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65 kA / LUB32 25 A @ 480 V AC | 30 kA / LUB12/32 12,5 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32430.html | www.woehner.com/en/products/32430.html
32429 | Sammelschienenadapter 16 A, angepasst auf Schaltgeräte | busbar adapter 16 A, aligned to switchgear | 05 | 21 | EEC6025 | 600 |  | 12 | [11 empty] | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32430.html | www.woehner.com/en/products/32430.html
32430 | Sammelschienenadapter 25 A | busbar adapter 25 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 65 kA / Comb. Motor Controller NKJH 16 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32431.html | www.woehner.com/en/products/32431.html
32430 | Sammelschienenadapter 25 A | busbar adapter 25 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 65 kA / Comb. Motor Controller NKJH 25 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32431.html | www.woehner.com/en/products/32431.html
32430 | Sammelschienenadapter 25 A | busbar adapter 25 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 30 kA / Comb. Motor Controller NKJH 12,5 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32431.html | www.woehner.com/en/products/32431.html
32430 | Sammelschienenadapter 25 A | busbar adapter 25 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 50 kA / Comb. Motor Controller NKJH 32 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32431.html | www.woehner.com/en/products/32431.html
32431 | Sammelschienenadapter 25 A | busbar adapter 25 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 50 kA / Comb. Motor Controller NKJH 32 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32432.html | www.woehner.com/en/products/32432.html
32431 | Sammelschienenadapter 25 A | busbar adapter 25 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 30 kA / Comb. Motor Controller NKJH 12,5 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32432.html | www.woehner.com/en/products/32432.html
32431 | Sammelschienenadapter 25 A | busbar adapter 25 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 65 kA / Comb. Motor Controller NKJH 25 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32432.html | www.woehner.com/en/products/32432.html
32431 | Sammelschienenadapter 25 A | busbar adapter 25 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 65 kA / Comb. Motor Controller NKJH 16 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32432.html | www.woehner.com/en/products/32432.html
32432 | Sammelschienenadapter 25 A | busbar adapter 25 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 30 kA / Comb. Motor Controller NKJH 12,5 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32433.html | www.woehner.com/en/products/32433.html
32432 | Sammelschienenadapter 25 A | busbar adapter 25 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 65 kA / Comb. Motor Controller NKJH 25 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32433.html | www.woehner.com/en/products/32433.html
32432 | Sammelschienenadapter 25 A | busbar adapter 25 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 65 kA / Comb. Motor Controller NKJH 16 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32433.html | www.woehner.com/en/products/32433.html
32432 | Sammelschienenadapter 25 A | busbar adapter 25 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 50 kA / Comb. Motor Controller NKJH 32 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32433.html | www.woehner.com/en/products/32433.html
32433 | Sammelschienenadapter 25 A | busbar adapter 25 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 50 kA / Comb. Motor Controller NKJH 32 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32434.html | www.woehner.com/en/products/32434.html
32433 | Sammelschienenadapter 25 A | busbar adapter 25 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 30 kA / Comb. Motor Controller NKJH 12,5 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32434.html | www.woehner.com/en/products/32434.html
32433 | Sammelschienenadapter 25 A | busbar adapter 25 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 65 kA / Comb. Motor Controller NKJH 25 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32434.html | www.woehner.com/en/products/32434.html
32433 | Sammelschienenadapter 25 A | busbar adapter 25 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 65 kA / Comb. Motor Controller NKJH 16 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32434.html | www.woehner.com/en/products/32434.html
32434 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65 kA / GV2P 25 A @ 480 V AC | 30 kA / GV2P 12,5 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32436.html | www.woehner.com/en/products/32436.html
32434 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65 kA / GV2P 25 A @ 480 V AC | 65 kA / GV2P 25 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32436.html | www.woehner.com/en/products/32436.html
32434 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65 kA / GV2P 25 A @ 480 V AC | 50 kA / GV2P 32 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32436.html | www.woehner.com/en/products/32436.html
32434 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65 kA / GV2P 25 A @ 480 V AC | 65 kA / GV2P 16 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32436.html | www.woehner.com/en/products/32436.html
32436 | Sammelschienenadapter 25 A | busbar adapter 25 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 30 kA / Comb. Motor Controller NKJH 12,5 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32438.html | www.woehner.com/en/products/32438.html
32436 | Sammelschienenadapter 25 A | busbar adapter 25 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 50 kA / Comb. Motor Controller NKJH 32 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32438.html | www.woehner.com/en/products/32438.html
32436 | Sammelschienenadapter 25 A | busbar adapter 25 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 65 kA / Comb. Motor Controller NKJH 16 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32438.html | www.woehner.com/en/products/32438.html
32436 | Sammelschienenadapter 25 A | busbar adapter 25 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 65 kA / Comb. Motor Controller NKJH 25 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32438.html | www.woehner.com/en/products/32438.html
32438 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65 kA / GV2P 25 A @ 480 V AC | 65 kA / GV2P 16 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32439.html | www.woehner.com/en/products/32439.html
32438 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65 kA / GV2P 25 A @ 480 V AC | 65 kA / GV2P 25 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32439.html | www.woehner.com/en/products/32439.html
32438 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65 kA / GV2P 25 A @ 480 V AC | 30 kA / GV2P 12,5 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32439.html | www.woehner.com/en/products/32439.html
32438 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65 kA / GV2P 25 A @ 480 V AC | 50 kA / GV2P 32 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32439.html | www.woehner.com/en/products/32439.html
32439 | Sammelschienenadapter 25 A | busbar adapter 25 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 50 kA / Comb. Motor Controller NKJH 32 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32440.html | www.woehner.com/en/products/32440.html
32439 | Sammelschienenadapter 25 A | busbar adapter 25 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 65 kA / Comb. Motor Controller NKJH 16 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32441.html | www.woehner.com/en/products/32441.html
32439 | Sammelschienenadapter 25 A | busbar adapter 25 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 30 kA / Comb. Motor Controller NKJH 12,5 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32442.html | www.woehner.com/en/products/32442.html
32439 | Sammelschienenadapter 25 A | busbar adapter 25 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 65 kA / Comb. Motor Controller NKJH 25 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32443.html | www.woehner.com/en/products/32443.html
32440 | Sammelschienenadapter 16 A, angepasst auf Schaltgeräte | busbar adapter 16 A, aligned to switchgear | 05 | 21 | EEC6025 | 600 |  | 12 | [11 empty] | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32444.html | www.woehner.com/en/products/32444.html
32441 | Sammelschienenadapter 32 A | busbar adapter 32 A | 05 | 21 | EEC6032-L | 600 |  | 30 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32445.html | www.woehner.com/en/products/32445.html
32442 | Sammelschienenadapter 32 A | busbar adapter 32 A | 05 | 21 | EEC6032-L | 600 |  | 30 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32445.html | www.woehner.com/en/products/32445.html
32443 | Sammelschienenadapter 32 A | busbar adapter 32 A | 05 | 21 | EEC6032-L | 600 |  | 30 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32445.html | www.woehner.com/en/products/32445.html
32444 | Sammelschienenadapter 32 A | busbar adapter 32 A | 05 | 21 | EEC6032-L | 600 |  | 30 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32445.html | www.woehner.com/en/products/32445.html
32445 | Sammelschienenadapter 25 A, angepasst auf Schaltgeräte | busbar adapter 25 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65k A / 3RV20 25 A @ 480 V AC | 30 kA / 3RV20 12,5 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32446.html | www.woehner.com/en/products/32446.html
32445 | Sammelschienenadapter 25 A, angepasst auf Schaltgeräte | busbar adapter 25 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65k A / 3RV20 25 A @ 480 V AC | 65 kA / 3RV20 16 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32448.html | www.woehner.com/en/products/32448.html
32445 | Sammelschienenadapter 25 A, angepasst auf Schaltgeräte | busbar adapter 25 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65k A / 3RV20 25 A @ 480 V AC | 65k A / 3RV20 25 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32448.html | www.woehner.com/en/products/32448.html
32445 | Sammelschienenadapter 25 A, angepasst auf Schaltgeräte | busbar adapter 25 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65k A / 3RV20 25 A @ 480 V AC | 50 kA / 3RV20 32 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32448.html | www.woehner.com/en/products/32448.html
32446 | Sammelschienenadapter 32 A | busbar adapter 32 A | 05 | 21 | EEC6032-L | 600 |  | 30 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32448.html | www.woehner.com/en/products/32448.html
32448 | Sammelschienenadapter 25 A, angepasst auf Schaltgeräte | busbar adapter 25 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65k A / 3RV20 25 A @ 480 V AC | 65k A / 3RV20 25 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32449.html | www.woehner.com/en/products/32449.html
32448 | Sammelschienenadapter 25 A, angepasst auf Schaltgeräte | busbar adapter 25 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65k A / 3RV20 25 A @ 480 V AC | 50 kA / 3RV20 32 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32450.html | www.woehner.com/en/products/32450.html
32448 | Sammelschienenadapter 25 A, angepasst auf Schaltgeräte | busbar adapter 25 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65k A / 3RV20 25 A @ 480 V AC | 65 kA / 3RV20 16 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32451.html | www.woehner.com/en/products/32451.html
32448 | Sammelschienenadapter 25 A, angepasst auf Schaltgeräte | busbar adapter 25 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65k A / 3RV20 25 A @ 480 V AC | 30 kA / 3RV20 12,5 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32452.html | www.woehner.com/en/products/32452.html
32449 | Sammelschienenadapter 32 A | busbar adapter 32 A | 05 | 21 | EEC6032-L | 600 |  | 30 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32453.html | www.woehner.com/en/products/32453.html
32450 | Sammelschienenadapter 25 A, angepasst auf Schaltgeräte | busbar adapter 25 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32454.html | www.woehner.com/en/products/32454.html
32451 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32455.html | www.woehner.com/en/products/32455.html
32452 | Sammelschienenadapter 25 A, angepasst auf Schaltgeräte | busbar adapter 25 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32456.html | www.woehner.com/en/products/32456.html
32453 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32457.html | www.woehner.com/en/products/32457.html
32454 | Sammelschienenadapter 63 A | busbar adapter 63 A | 05 | 24 | EEC6063-L | 600 |  | 65 |  |  |  |  | 7,5 | 3 cycles (without OPD) @ 600 V AC | 100 | 100 kA / fuse Class CF, J or T 60 A @ 600 V AC |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32459.html | www.woehner.com/en/products/32459.html
32455 | Sammelschienenadapter 63 A | busbar adapter 63 A | 05 | 24 | EEC6063-L | 600 |  | 65 |  |  |  |  | 7,5 | 3 cycles (without OPD) @ 600 V AC | 100 | 100 kA / fuse Class CF, J or T 60 A @ 600 V AC |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32460.html | www.woehner.com/en/products/32460.html
32456 | Sammelschienenadapter 63 A | busbar adapter 63 A | 05 | 24 | EEC6063-L | 600 |  | 65 |  |  |  |  | 7,5 | 3 cycles (without OPD) @ 600 V AC | 100 | 100 kA / fuse Class CF, J or T 60 A @ 600 V AC |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32461.html | www.woehner.com/en/products/32461.html
32457 | Sammelschienenadapter 63 A | busbar adapter 63 A | 05 | 24 | EEC6063-L | 600 |  | 65 |  |  |  |  | 7,5 | 3 cycles (without OPD) @ 600 V AC | 100 | 100 kA / fuse Class CF, J or T 60 A @ 600 V AC |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32463.html | www.woehner.com/en/products/32463.html
32459 | Sammelschienenadapter 63 A | busbar adapter 63 A | 05 | 24 | EEC6063-L | 600 |  | 65 |  |  |  |  | 7,5 | 3 cycles (without OPD) @ 600 V AC | 100 | 100 kA / fuse Class CF, J or T 60 A @ 600 V AC |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32464.html | www.woehner.com/en/products/32464.html
32460 | Sammelschienenadapter 63 A, angepasst auf Schaltgeräte | busbar adapter 63 A, aligned to switchgear | 05 | 24 | EEC6063-L | 600 |  | 65 |  |  |  |  | 7,5 | 3 cycles (without OPD) @ 600 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32465.html | www.woehner.com/en/products/32465.html
32461 | Sammelschienenadapter 63 A | busbar adapter 63 A | 05 | 24 | EEC6063-L | 600 |  | 65 |  |  |  |  | 7,5 | 3 cycles (without OPD) @ 600 V AC | 100 | 100 kA / fuse Class CF, J or T 60 A @ 600 V AC |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32466.html | www.woehner.com/en/products/32466.html
32463 | Sammelschienenadapter 63 A, angepasst auf Schaltgeräte | busbar adapter 63 A, aligned to switchgear | 05 | 24 | EEC6063-L | 600 |  | 65 |  |  |  |  | 7,5 | 3 cycles (without OPD) @ 600 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32467.html | www.woehner.com/en/products/32467.html
32464 | Sammelschienenadapter 80 A | busbar adapter 80 A | 05 | 27 | EEC6080 | 600 |  | 80 | [11 empty] | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32469.html | www.woehner.com/en/products/32469.html
32465 | Sammelschienenadapter 80 A | busbar adapter 80 A | 05 | 27 | EEC6080 | 600 |  | 80 | [11 empty] | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32471.html | www.woehner.com/en/products/32471.html
32466 | Sammelschienenadapter 80 A | busbar adapter 80 A | 05 | 27 | EEC6080-L | 600 |  | 80 |  |  |  |  | 10 | 3 cycles (without OPD) @ 600 V AC | 100 | 100 kA / fuse Class CF, J or T 150 A @ 600 V AC |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32472.html | www.woehner.com/en/products/32472.html
32467 | Sammelschienenadapter 80 A | busbar adapter 80 A | 05 | 27 | EEC6080-L | 600 |  | 80 |  |  |  |  | 10 | 3 cycles (without OPD) @ 600 V AC | 100 | 100 kA / fuse Class CF, J or T 150 A @ 600 V AC |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32477.html | www.woehner.com/en/products/32477.html
32469 | Sammelschienenadapter 80 A | busbar adapter 80 A | 05 | 27 | EEC6080-L | 600 |  | 80 |  |  |  |  | 10 | 3 cycles (without OPD) @ 600 V AC | 100 | 100 kA / fuse Class CF, J or T 150 A @ 600 V AC |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32478.html | www.woehner.com/en/products/32478.html
32471 | Sammelschienenadapter 80 A | busbar adapter 80 A | 05 | 27 | EEC6080 | 600 |  | 80 | [9 empty] | Yes |  | UL recognized | E123577 | NMTR2 | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32484.html | www.woehner.com/en/products/32484.html
32472 | Sammelschienenadapter 80 A | busbar adapter 80 A | 05 | 27 | EEC6080-L | 600 |  | 80 |  |  |  |  | 10 | 3 cycles (without OPD) @ 600 V AC | 100 | 100 kA / fuse Class CF, J or T 150 A @ 600 V AC |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32485.html | www.woehner.com/en/products/32485.html
32477 | Sammelschienengeräteträger | busbar component support | 05 | 17 | EEC6000-L | 600 | [11 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32498.html | www.woehner.com/en/products/32498.html
32478 | Sammelschienengeräteträger | busbar component support | 05 | 17 | EEC6000-L | 600 | [11 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32516.html | www.woehner.com/en/products/32516.html
32484 | Sammelschienengeräteträger | busbar component support | 05 | 17 | EEC6000-L | 600 | [11 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32533.html | www.woehner.com/en/products/32533.html
32485 | Sammelschienengeräteträger | busbar component support | 05 | 17 | EEC6000-L | 600 | [11 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32534.html | www.woehner.com/en/products/32534.html
32498 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32535.html | www.woehner.com/en/products/32535.html
32516 | Sammelschienenadapter 63 A | busbar adapter 63 A | 05 | 27 | EEC 6080 | 600 |  | 63 | [9 empty] | Yes |  | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32570.html | www.woehner.com/en/products/32570.html
32533 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 30 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32571.html | www.woehner.com/en/products/32571.html
32534 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32575.html | www.woehner.com/en/products/32575.html
32535 | Sammelschienenadapter 63 A, angepasst auf Schaltgeräte | busbar adapter 63 A, aligned to switchgear | 05 | 24 | EEC6063-L | 600 |  | 65 |  |  |  |  | 7,5 | 3 cycles (without OPD) @ 600 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32577.html | www.woehner.com/en/products/32577.html
32570 | Sammelschienenadapter 160 A, 3-polig, mit CrossLink®-Schnittstelle, angepasst auf Schaltgeräte | busbar adapter 160 A, 3-pole, with CrossLink® interface, aligned to switchgear | 05 | 30 | ECL60160-L | 600 |  | 160 | [8 empty] | 35 kA @ NZMN1_125A 480V | Yes |  | UL listed | E353754 | DHWZ | DIHS7 | [5 empty] | www.woehner.com/de/products/32578.html | www.woehner.com/en/products/32578.html
32571 | Sammelschienenadapter 160 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 160 A, 3-pole, aligned to switchgear | 05 | 30 | EPC60160 | 600 |  | 160 | [8 empty] | 35kA @ circuit breaker DIVQ/7 125A, 480Vac | Yes |  | UL recognized | E123577 | NMTR2 | NMTR8 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32579.html | www.woehner.com/en/products/32579.html
32575 | Sammelschienenadapter 160 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 160 A, 3-pole, aligned to switchgear | 05 | 30 | EPC60160-L | 600 |  | 160 | [8 empty] | 35kA @ circuit breaker DIVQ/7 125A, 480Vac | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32580.html | www.woehner.com/en/products/32580.html
32577 | Sammelschienenadapter 160 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 160 A, 3-pole, aligned to switchgear | 05 | 30 | EPC60160-L | 600 |  | 160 | [8 empty] | 35kA @ circuit breaker DIVQ/7 125A, 480Vac | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32581.html | www.woehner.com/en/products/32581.html
32578 | Sammelschienenadapter 250 A, 4-polig, angepasst auf Schaltgeräte | busbar adapter 250 A, 4-pole, aligned to switchgear | 05 | 36 | EPC60250-L | 600 |  | 250 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32582.html | www.woehner.com/en/products/32582.html
32579 | Sammelschienenadapter 400 A, 4-polig, angepasst auf Schaltgeräte | busbar adapter 400 A, 4-pole, aligned to switchgear | 05 | 42 | EPC60630-L | 600 |  | 630 |  |  |  |  | 30 |  |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32583.html | www.woehner.com/en/products/32583.html
32580 | Sammelschienenadapter 250 A, 4-polig, angepasst auf Schaltgeräte | busbar adapter 250 A, 4-pole, aligned to switchgear | 05 | 36 | EPC60250-L | 600 |  | 250 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32584.html | www.woehner.com/en/products/32584.html
32581 | Sammelschienenadapter 500 A, 4-polig, angepasst auf Schaltgeräte | busbar adapter 500 A, 4-pole, aligned to switchgear | 05 | 42 | EPC60630-L | 600 |  | 630 |  |  |  |  | 30 |  |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32585.html | www.woehner.com/en/products/32585.html
32582 | Sammelschienenadapter 250 A, 4-polig, angepasst auf Schaltgeräte | busbar adapter 250 A, 4-pole, aligned to switchgear | 05 | 36 | EPC60250-L | 600 |  | 250 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32586.html | www.woehner.com/en/products/32586.html
32583 | Sammelschienenadapter 500 A, 4-polig, angepasst auf Schaltgeräte | busbar adapter 500 A, 4-pole, aligned to switchgear | 05 | 42 | EPC60630-L | 600 |  | 630 |  |  |  |  | 30 |  |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32588.html | www.woehner.com/en/products/32588.html
32584 | Sammelschienenadapter 250 A, 4-polig, angepasst auf Schaltgeräte | busbar adapter 250 A, 4-pole, aligned to switchgear | 05 | 36 | EPC60250-L | 600 |  | 250 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32588.html | www.woehner.com/en/products/32588.html
32585 | Sammelschienenadapter 500 A, 4-polig, angepasst auf Schaltgeräte | busbar adapter 500 A, 4-pole, aligned to switchgear | 05 | 42 | EPC60630-L | 600 |  | 630 |  |  |  |  | 30 |  |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32588.html | www.woehner.com/en/products/32588.html
32586 | Sammelschienenadapter 250 A, 4-polig, angepasst auf Schaltgeräte | busbar adapter 250 A, 4-pole, aligned to switchgear | 05 | 36 | EPC60250-L | 600 |  | 250 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32588.html | www.woehner.com/en/products/32588.html
32588 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 30 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65k A / 3RV20 25 A @ 480 V AC | 65 kA / 3RV20 16 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32590.html | www.woehner.com/en/products/32590.html
32588 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 30 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65k A / 3RV20 25 A @ 480 V AC | 65k A / 3RV20 25 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32590.html | www.woehner.com/en/products/32590.html
32588 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 30 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65k A / 3RV20 25 A @ 480 V AC | 30 kA / 3RV20 12,5 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32590.html | www.woehner.com/en/products/32590.html
32588 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 30 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65k A / 3RV20 25 A @ 480 V AC | 50 kA / 3RV20 32 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32590.html | www.woehner.com/en/products/32590.html
32590 | Sammelschienenadapter 32 A | busbar adapter 32 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 30 kA / Comb. Motor Controller NKJH 12,5 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32591.html | www.woehner.com/en/products/32591.html
32590 | Sammelschienenadapter 32 A | busbar adapter 32 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 50 kA / Comb. Motor Controller NKJH 32 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32592.html | www.woehner.com/en/products/32592.html
32590 | Sammelschienenadapter 32 A | busbar adapter 32 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 65 kA / Comb. Motor Controller NKJH 16 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32593.html | www.woehner.com/en/products/32593.html
32590 | Sammelschienenadapter 32 A | busbar adapter 32 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 65 kA / Comb. Motor Controller NKJH 25 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32598.html | www.woehner.com/en/products/32598.html
32591 | Sammelschienenadapter 63 A | busbar adapter 63 A | 05 | 24 | EEC6063C-L | 600 |  | 65 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32601.html | www.woehner.com/en/products/32601.html
32592 | Sammelschienenadapter 250 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 250 A, 3-pole, aligned to switchgear | 05 | 36 | EPC60250-L | 600 |  | 250 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32635.html | www.woehner.com/en/products/32635.html
32593 | Sammelschienenadapter 580 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 580 A, 3-pole, aligned to switchgear | 05 | 42 | EPC60630-L | 600 |  | 630 |  |  |  |  | 30 |  |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32636.html | www.woehner.com/en/products/32636.html
32598 | Sammelschienenadapter 80 A | busbar adapter 80 A | 05 | 27 | EEC6063-L | 600 |  | 80 |  |  |  |  | 7,5 | 3 cycles (without OPD) @ 600 V AC | 100 | 100 kA / fuse Class CF, J or T 60 A @ 600 V AC |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32637.html | www.woehner.com/en/products/32637.html
32601 | Sammelschienenadapter 290 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 290 A, 3-pole, aligned to switchgear | 05 | 36 | EPC60250-L | 600 |  | 250 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32637.html | www.woehner.com/en/products/32637.html
32635 | Sammelschienengeräteträger | busbar component support | 05 | 17 | EEC6000-L | 600 | [11 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32637.html | www.woehner.com/en/products/32637.html
32636 | Sammelschienengeräteträger | busbar component support | 05 | 17 | EEC6000-L | 600 | [11 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32637.html | www.woehner.com/en/products/32637.html
32637 | Sammelschienenadapter 25 A, angepasst auf Schaltgeräte | busbar adapter 25 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65k A / 3RV20 25 A @ 480 V AC | 65 kA / 3RV20 16 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32638.html | www.woehner.com/en/products/32638.html
32637 | Sammelschienenadapter 25 A, angepasst auf Schaltgeräte | busbar adapter 25 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65k A / 3RV20 25 A @ 480 V AC | 65k A / 3RV20 25 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32639.html | www.woehner.com/en/products/32639.html
32637 | Sammelschienenadapter 25 A, angepasst auf Schaltgeräte | busbar adapter 25 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65k A / 3RV20 25 A @ 480 V AC | 30 kA / 3RV20 12,5 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32641.html | www.woehner.com/en/products/32641.html
32637 | Sammelschienenadapter 25 A, angepasst auf Schaltgeräte | busbar adapter 25 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65k A / 3RV20 25 A @ 480 V AC | 50 kA / 3RV20 32 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32642.html | www.woehner.com/en/products/32642.html
32638 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32643.html | www.woehner.com/en/products/32643.html
32639 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32650.html | www.woehner.com/en/products/32650.html
32641 | Sammelschienenadapter 600 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 600 A, 3-pole, aligned to switchgear | 05 | 42 | EPC60630-L | 600 |  | 630 |  |  |  |  | 30 |  |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32650.html | www.woehner.com/en/products/32650.html
32642 | Sammelschienenadapter 230 A, 4-polig, angepasst auf Schaltgeräte | busbar adapter 230 A, 4-pole, aligned to switchgear | 05 | 36 | EPC60250-L |  |  | 250 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32650.html | www.woehner.com/en/products/32650.html
32643 | Sammelschienenadapter 520 A, 4-polig, angepasst auf Schaltgeräte | busbar adapter 520 A, 4-pole, aligned to switchgear | 05 | 42 | 60630.1-L | 600 |  | 520 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32650.html | www.woehner.com/en/products/32650.html
32650 | Sammelschienenadapter 25 A, angepasst auf Schaltgeräte | busbar adapter 25 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65k A / 3RV20 25 A @ 480 V AC | 50 kA / 3RV20 32 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32651.html | www.woehner.com/en/products/32651.html
32650 | Sammelschienenadapter 25 A, angepasst auf Schaltgeräte | busbar adapter 25 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65k A / 3RV20 25 A @ 480 V AC | 65k A / 3RV20 25 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32655.html | www.woehner.com/en/products/32655.html
32650 | Sammelschienenadapter 25 A, angepasst auf Schaltgeräte | busbar adapter 25 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65k A / 3RV20 25 A @ 480 V AC | 65 kA / 3RV20 16 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32655.html | www.woehner.com/en/products/32655.html
32650 | Sammelschienenadapter 25 A, angepasst auf Schaltgeräte | busbar adapter 25 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | 65k A / 3RV20 25 A @ 480 V AC | 30 kA / 3RV20 12,5 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32655.html | www.woehner.com/en/products/32655.html
32655 | Sammelschienenadapter 32 A | busbar adapter 32 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 50 kA / Comb. Motor Controller NKJH 32 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32655.html | www.woehner.com/en/products/32655.html
32655 | Sammelschienenadapter 32 A | busbar adapter 32 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 30 kA / Comb. Motor Controller NKJH 12,5 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32659.html | www.woehner.com/en/products/32659.html
32655 | Sammelschienenadapter 32 A | busbar adapter 32 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 65 kA / Comb. Motor Controller NKJH 25 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32662.html | www.woehner.com/en/products/32662.html
32655 | Sammelschienenadapter 32 A | busbar adapter 32 A | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | Comb. Motor Controller NKJH 25 A @ 480 V AC | 65 kA / Comb. Motor Controller NKJH 16 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32663.html | www.woehner.com/en/products/32663.html
32659 | Sammelschienenadapter 32 A, angepasst auf Schaltgeräte | busbar adapter 32 A, aligned to switchgear | 05 | 21 | EEC6025-L | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32665.html | www.woehner.com/en/products/32665.html
32662 | Sammelschienenadapter 80 A, angepasst auf Schaltgeräte | busbar adapter 80 A, aligned to switchgear | 05 | 27 | EEC60100-L | 600 |  | 80 | [9 empty] | Yes |  | UL listed | E123577 | NMTR | [6 empty] | www.woehner.com/de/products/32666.html | www.woehner.com/en/products/32666.html
32663 | Sammelschienenadapter 80 A, angepasst auf Schaltgeräte | busbar adapter 80 A, aligned to switchgear | 05 | 27 | EEC60100-L | 600 |  | 80 | [8 empty] | 65kA @ circuit breakerSiemens S3 | Yes |  | UL listed | E123577 | NMTR | [6 empty] | www.woehner.com/de/products/32668.html | www.woehner.com/en/products/32668.html
32665 | Geräteträger mit CrossLink®-Schnittstelle | component support with CrossLink® interface | 05 | 17 | [15 empty] | UL listed | E123577 | NMTR | [6 empty] | www.woehner.com/de/products/32669.html | www.woehner.com/en/products/32669.html
32666 | Adapter 16 A, mit CrossLink®-Schnittstelle | adapter 16 A, with CrossLink® interface | 05 | 21 | EQ45-AA | 600 |  | 12 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | any NKJH/7 12 A @ 480 V AC | 50 kA / Class CC 12 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32676.html | www.woehner.com/en/products/32676.html
32666 | Adapter 16 A, mit CrossLink®-Schnittstelle | adapter 16 A, with CrossLink® interface | 05 | 21 | EQ45-AA | 600 |  | 12 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | any NKJH/7 12 A @ 480 V AC | 65 kA / NKJH/7 12 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32682.html | www.woehner.com/en/products/32682.html
32668 | Adapter 16 A, mit CrossLink®-Schnittstelle | adapter 16 A, with CrossLink® interface | 05 | 21 | EQ45-BA | 600 |  | 12 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | any NKJH/7 12 A @ 480 V AC | 65 kA / NKJH/7 12 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32684.html | www.woehner.com/en/products/32684.html
32668 | Adapter 16 A, mit CrossLink®-Schnittstelle | adapter 16 A, with CrossLink® interface | 05 | 21 | EQ45-BA | 600 |  | 12 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | any NKJH/7 12 A @ 480 V AC | 50 kA / Class CC 12 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32686.html | www.woehner.com/en/products/32686.html
32669 | Adapter 16 A, mit CrossLink®-Schnittstelle | Adapter 16 A, with CrossLink® interface | 05 | 21 | EQ45-BA | 600 |  | 12 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | any NKJH/7 12 A @ 480 V AC | 50 kA / Class CC 12 A @ 600 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32692.html | www.woehner.com/en/products/32692.html
32669 | Adapter 16 A, mit CrossLink®-Schnittstelle | Adapter 16 A, with CrossLink® interface | 05 | 21 | EQ45-BA | 600 |  | 12 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | any NKJH/7 12 A @ 480 V AC | 65 kA / NKJH/7 12 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32718.html | www.woehner.com/en/products/32718.html
32676 | Adapter 25 A, mit CrossLink®-Schnittstelle | adapter 25 A, with CrossLink® interface | 05 | 21 | EQ45-BB | 600 |  | 25 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | any NKJH/7 32 A @ 480 V AC | 65 kA / NKJH/7 32 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32719.html | www.woehner.com/en/products/32719.html
32682 | Adapter 32 A, mit CrossLink®-Schnittstelle | adapter 32 A, with CrossLink® interface | 05 | 21 | EQ45-AC | 600 |  | 30 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | any NKJH/7 32 A @ 480 V AC | 65 kA / NKJH/7 32 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32720.html | www.woehner.com/en/products/32720.html
32684 | Adapter 32 A, mit CrossLink®-Schnittstelle | adapter 32 A, with CrossLink® interface | 05 | 21 | EQ45-BC | 600 |  | 30 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | any NKJH/7 32 A @ 480 V AC | 65 kA / NKJH/7 32 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32721.html | www.woehner.com/en/products/32721.html
32686 | Adapter 32 A, mit CrossLink®-Schnittstelle | Adapter 32 A, with CrossLink® interface | 05 | 21 | EQ45-BC | 600 |  | 30 |  |  |  |  | 5 | 3 cycles (without OPD) @ 600 V AC | 65 | any NKJH/7 32 A @ 480 V AC | 65 kA / NKJH/7 32 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32722.html | www.woehner.com/en/products/32722.html
32690 | Adapter 160 A, mit CrossLink®-Schnittstelle | adapter 160 A, with CrossLink® interface | 05 | 30 | EQ90-AA | 600 |  | 100 | [6 empty] | 65 | 65 kA / MCCB DIVQ/7 125 A @ 480 V AC |  |  |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32723.html | www.woehner.com/en/products/32723.html
32691 | Adapter 160 A, mit CrossLink®-Schnittstelle | adapter 160 A, with CrossLink® interface | 05 | 30 | EQ90-AA | 600 |  | 100 | [6 empty] | 65 | 65 kA / MCCB DIVQ/7 125 A @ 480 V AC |  |  |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32724.html | www.woehner.com/en/products/32724.html
32692 | Adapter 45 A, mit CrossLink®-Schnittstelle | adapter 45 A, with CrossLink® interface | 05 | 24 | EQ45-BD | 600 |  | 45 |  |  |  |  | 6 | 3 cycles (without OPD) @ 600 V AC | 65 | any NKJH/7 55 A @ 480 V AC | 65 kA / NKJH/7 55 A @ 480 V AC | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32725.html | www.woehner.com/en/products/32725.html
32718 | Sammelschienenadapter 1400 A | busbar adapter 1400 A | 05 | 48 | EQ185-A1600-C | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32726.html | www.woehner.com/en/products/32726.html
32719 | Sammelschienenadapter 1200 A | busbar adapter 1200 A | 05 | 48 | EQ185-A1600-C | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32729.html | www.woehner.com/en/products/32729.html
32720 | Sammelschienenadapter 1400 A | busbar adapter 1400 A | 05 | 48 | EQ185-A1600-S | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32730.html | www.woehner.com/en/products/32730.html
32721 | Sammelschienenadapter 1200 A | busbar adapter 1200 A | 05 | 48 | EQ185-A1600-S | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32731.html | www.woehner.com/en/products/32731.html
32722 | Sammelschienenadapter 1320 A | busbar adapter 1320 A | 05 | 48 | EQ185-A1600-C | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32732.html | www.woehner.com/en/products/32732.html
32723 | Sammelschienenadapter 1220 A | busbar adapter 1220 A | 05 | 48 | EQ185-A1600-C | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32733.html | www.woehner.com/en/products/32733.html
32724 | Sammelschienenadapter 1320 A | busbar adapter 1320 A | 05 | 48 | EQ185-A1600-S | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32734.html | www.woehner.com/en/products/32734.html
32725 | Sammelschienenadapter 1220 A | busbar adapter 1220 A | 05 | 48 | EQ185-A1600-S | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32737.html | www.woehner.com/en/products/32737.html
32726 | Sammelschienenadapter 1220 A | busbar adapter 1220 A | 05 | 48 | EQ185-A1600-C | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32738.html | www.woehner.com/en/products/32738.html
32729 | Sammelschienenadapter 1000 A | busbar adapter 1000 A | 05 | 48 | EQ185-A1000-C | 1000 |  | 800 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32739.html | www.woehner.com/en/products/32739.html
32730 | Sammelschienenadapter 800 A | busbar adapter 800 A | 05 | 48 | EQ185-A1000-C | 1000 |  | 800 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32741.html | www.woehner.com/en/products/32741.html
32731 | Sammelschienenadapter 1400 A | busbar adapter 1400 A | 05 | 48 | EQ185-A1600-C | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32742.html | www.woehner.com/en/products/32742.html
32732 | Sammelschienenadapter 1200 A | busbar adapter 1200 A | 05 | 48 | EQ185-A1600-C | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32743.html | www.woehner.com/en/products/32743.html
32733 | Sammelschienenadapter 1000 A | busbar adapter 1000 A | 05 | 48 | EQ185-A1000-C | 1000 |  | 800 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32745.html | www.woehner.com/en/products/32745.html
32734 | Sammelschienenadapter 1400 A | busbar adapter 1400 A | 05 | 48 | EQ185-A1600-C | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32746.html | www.woehner.com/en/products/32746.html
32737 | Sammelschienenadapter 1200 A | busbar adapter 1200 A | 05 | 48 | EQ185-A1600-C | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32747.html | www.woehner.com/en/products/32747.html
32738 | Sammelschienenadapter 1320 A | busbar adapter 1320 A | 05 | 48 | EQ185-A1600-C | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32748.html | www.woehner.com/en/products/32748.html
32739 | Sammelschienenadapter 1150 A | busbar adapter 1150 A | 05 | 48 | EQ185-A1600-C | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32749.html | www.woehner.com/en/products/32749.html
32741 | Sammelschienenadapter 630 A | busbar adapter 630 A | 05 | 48 | EQ185-A630-C | 1000 | 1000 | 630 |  |  |  |  | 22 | 3 cycles (without OPD) @ 600 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32752.html | www.woehner.com/en/products/32752.html
32742 | Sammelschienenadapter 630 A | busbar adapter 630 A | 05 | 48 | EQ185-A630-C | 1000 | 1000 | 630 |  |  |  |  | 22 | 3 cycles (without OPD) @ 600 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32753.html | www.woehner.com/en/products/32753.html
32743 | Sammelschienenadapter 630 A | busbar adapter 630 A | 05 | 48 | EQ185-A630-S | 1000 | 1000 | 630 |  |  |  |  | 22 | 3 cycles (without OPD) @ 600 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32754.html | www.woehner.com/en/products/32754.html
32745 | Sammelschienenadapter 630 A | busbar adapter 630 A | 05 | 48 | EQ185-A630-C | 1000 | 1000 | 630 |  |  |  |  | 22 | 3 cycles (without OPD) @ 600 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32755.html | www.woehner.com/en/products/32755.html
32746 | Sammelschienenadapter 630 A | busbar adapter 630 A | 05 | 48 | EQ185-A630-C | 1000 | 1000 | 630 |  |  |  |  | 22 | 3 cycles (without OPD) @ 600 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32756.html | www.woehner.com/en/products/32756.html
32747 | Sammelschienenadapter 900 A | busbar adapter 900 A | 05 | 48 | EQ185-A1000-C | 1000 |  | 800 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32757.html | www.woehner.com/en/products/32757.html
32748 | Sammelschienenadapter 1320 A | busbar adapter 1320 A | 05 | 48 | EQ185-A1600-S | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32758.html | www.woehner.com/en/products/32758.html
32749 | Sammelschienenadapter 1150 A | busbar adapter 1150 A | 05 | 48 | EQ185-A1600-S | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32761.html | www.woehner.com/en/products/32761.html
32752 | Sammelschienenadapter 1550 A | busbar adapter 1550 A | 05 | 48 | EQ185-A1600-C | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32762.html | www.woehner.com/en/products/32762.html
32753 | Sammelschienenadapter 1150 A | busbar adapter 1150 A | 05 | 48 | EQ185-A1600-C | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32763.html | www.woehner.com/en/products/32763.html
32754 | Sammelschienenadapter 720 A | busbar adapter 720 A | 05 | 48 | EQ185-A1000-C | 1000 |  | 800 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32764.html | www.woehner.com/en/products/32764.html
32755 | Sammelschienenadapter 1000 A | busbar adapter 1000 A | 05 | 48 | EQ185-A1000-C | 1000 |  | 800 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32765.html | www.woehner.com/en/products/32765.html
32756 | Sammelschienenadapter 1450 A | busbar adapter 1450 A | 05 | 48 | EQ185-A1600-C | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32766.html | www.woehner.com/en/products/32766.html
32757 | Sammelschienenadapter 1250 A | busbar adapter 1250 A | 05 | 48 | EQ185-A1600-C | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32767.html | www.woehner.com/en/products/32767.html
32758 | Sammelschienenadapter 1000 A | busbar adapter 1000 A | 05 | 48 | EQ185-A1000-C | 1000 |  | 800 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32769.html | www.woehner.com/en/products/32769.html
32761 | Sammelschienenadapter 1440 A | busbar adapter 1440 A | 05 | 48 | EQ185-A1600-C | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32770.html | www.woehner.com/en/products/32770.html
32762 | Sammelschienenadapter 1250 A | busbar adapter 1250 A | 05 | 48 | EQ185-A1600-C | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32771.html | www.woehner.com/en/products/32771.html
32763 | Sammelschienenadapter 1000 A | busbar adapter 1000 A | 05 | 48 | EQ185-A1000-C | 1000 |  | 800 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32772.html | www.woehner.com/en/products/32772.html
32764 | Sammelschienenadapter 1500 A | busbar adapter 1500A | 05 | 48 | EQ185-A1600-C | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32773.html | www.woehner.com/en/products/32773.html
32765 | Sammelschienenadapter 1250 A | busbar adapter 1250 A | 05 | 48 | EQ185-A1600-C | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32774.html | www.woehner.com/en/products/32774.html
32766 | Sammelschienenadapter 1000 A | busbar adapter 1000 A | 05 | 48 | EQ185-A1000-C | 1000 |  | 800 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32775.html | www.woehner.com/en/products/32775.html
32767 | Sammelschienenadapter 800 A | busbar adapter 800 A | 05 | 48 | EQ185-A1000-C | 1000 |  | 800 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32776.html | www.woehner.com/en/products/32776.html
32769 | Sammelschienenadapter 630 A | busbar adapter 630 A | 05 | 48 | EQ185-A1000-C | 1000 |  | 800 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32777.html | www.woehner.com/en/products/32777.html
32770 | Sammelschienenadapter 630 A | busbar adapter 630 A | 05 | 48 | EQ185-A1000-S | 1000 |  | 800 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32779.html | www.woehner.com/en/products/32779.html
32771 | Sammelschienenadapter 1150 A | busbar adapter 1150 A | 05 | 48 | EQ185-A1600-C | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32780.html | www.woehner.com/en/products/32780.html
32772 | Sammelschienenadapter 1150 A | busbar adapter 1150 A | 05 | 48 | EQ185-A1600-S | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32781.html | www.woehner.com/en/products/32781.html
32773 | Sammelschienenadapter 1000 A | busbar adapter 1000 A | 05 | 48 | EQ185-A1000-S | 1000 |  | 800 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32783.html | www.woehner.com/en/products/32783.html
32774 | Sammelschienenadapter 650 A | busbar adapter 650A | 05 | 48 | EQ185-A1000-S | 1000 |  | 800 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32784.html | www.woehner.com/en/products/32784.html
32775 | Sammelschienenadapter 1400 A | busbar adapter 1400 A | 05 | 48 | EQ185-A1600-S | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32785.html | www.woehner.com/en/products/32785.html
32776 | Sammelschienenadapter 1200 A | busbar adapter 1200 A | 05 | 48 | EQ185-A1600-S | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32786.html | www.woehner.com/en/products/32786.html
32777 | Sammelschienenadapter 900 A | busbar adapter 900 A | 05 | 48 | EQ185-A1000-S | 1000 |  | 800 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32787.html | www.woehner.com/en/products/32787.html
32779 | Sammelschienenadapter 1000 A | busbar adapter 1000 A | 05 | 48 | EQ185-A1000-S | 1000 |  | 800 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32788.html | www.woehner.com/en/products/32788.html
32780 | Sammelschienenadapter 1400 A | busbar adapter 1400 A | 05 | 48 | EQ185-A1600-S | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32789.html | www.woehner.com/en/products/32789.html
32781 | Sammelschienenadapter 1200 A | busbar adapter 1200 A | 05 | 48 | EQ185-A1600-S | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32790.html | www.woehner.com/en/products/32790.html
32783 | Sammelschienenadapter 1000 A | busbar adapter 1000 A | 05 | 48 | EQ185-A1000-C | 1000 |  | 800 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32795.html | www.woehner.com/en/products/32795.html
32784 | Sammelschienenadapter 1220 A | busbar adapter 1220 A | 05 | 48 | EQ185-A1600-S | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32796.html | www.woehner.com/en/products/32796.html
32785 | Sammelschienenadapter 1000 A | busbar adapter 1000 A | 05 | 48 | EQ185-A1000-S | 1000 |  | 800 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32797.html | www.woehner.com/en/products/32797.html
32786 | Sammelschienenadapter 800 A | busbar adapter 800 A | 05 | 48 | EQ185-A1000-S | 1000 |  | 800 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32807.html | www.woehner.com/en/products/32807.html
32787 | Sammelschienenadapter 1400 A | busbar adapter 1400 A | 05 | 48 | EQ185-A1600-C | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32808.html | www.woehner.com/en/products/32808.html
32788 | Sammelschienenadapter 1200 A | busbar adapter 1200 A | 05 | 48 | EQ185-A1600-C | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32809.html | www.woehner.com/en/products/32809.html
32789 | Sammelschienenadapter 1400 A | busbar adapter 1400 A | 05 | 48 | EQ185-A1600-S | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32947.html | www.woehner.com/en/products/32947.html
32790 | Sammelschienenadapter 1200 A | busbar adapter 1200 A | 05 | 48 | EQ185-A1600-S | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32948.html | www.woehner.com/en/products/32948.html
32795 | Sammelschienenadapter 650 A | busbar adapter 650 A | 05 | 48 | EQ185-A1000-C | 1000 |  | 800 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32949.html | www.woehner.com/en/products/32949.html
32796 | Sammelschienenadapter 630 A | busbar adapter 630 A | 05 | 48 | EQ185-A1000-C | 1000 |  | 800 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32950.html | www.woehner.com/en/products/32950.html
32797 | Sammelschienenadapter 1320 A | busbar adapter 1320 A | 05 | 48 | EQ185-A1600-C | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32951.html | www.woehner.com/en/products/32951.html
32807 | Sammelschienenadapter 1320 A | busbar adapter 1320 A | 05 | 48 | EQ185-A1600-C | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32954.html | www.woehner.com/en/products/32954.html
32808 | Sammelschienenadapter 1320 A | busbar adapter 1320 A | 05 | 48 | EQ185-A1600-S | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32973.html | www.woehner.com/en/products/32973.html
32809 | Sammelschienenadapter 1440 A | busbar adapter 1400 A | 05 | 48 | EQ185-A1600-S | 1000 |  | 1200 |  |  |  |  | 50 | 3 cycles (without OPD) @ 1000 V AC |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/32974.html | www.woehner.com/en/products/32974.html
32947 | Tragschiene 45 mm | mounting rail 45 mm | 05 | 57 | TS35-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32975.html | www.woehner.com/en/products/32975.html
32948 | Tragschiene 54 mm | mounting rail 54 mm | 05 | 57 | TS35-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32976.html | www.woehner.com/en/products/32976.html
32949 | Tragschiene 63 mm | mounting rail 63 mm | 05 | 57 | TS35-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32976.html | www.woehner.com/en/products/32976.html
32950 | Tragschiene 72 mm | mounting rail 72 mm | 05 | 57 | TS35-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32977.html | www.woehner.com/en/products/32977.html
32951 | Tragschiene 81 mm | mounting rail 81 mm | 05 | 57 | TS35-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32978.html | www.woehner.com/en/products/32978.html
32954 | Verbindungselement, universell | connecting element, universal | 05 | 57 | X-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/32981.html | www.woehner.com/en/products/32981.html
32973 | UL-Klemmenaufsatz | terminal cap for UL | 05 | 57 | EEC25-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/33075.html | www.woehner.com/en/products/33075.html
32974 | UL-Klemmenaufsatz | terminal cap for UL | 05 | 57 | EEC80-L | [12 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/33079.html | www.woehner.com/en/products/33079.html
32975 | Sammelschienenadapter 400 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 400 A, 3-pole, aligned to switchgear | 05 | 42 | 60630.1-L | 600 |  | 540 | [6 empty] | 200 | 200kA @ 3VL4 600V |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/33149.html | www.woehner.com/en/products/33149.html
32976 | Sammelschienenadapter 160 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 160 A, 3-pole, aligned to switchgear | 05 | 36 | 60250.1-L | 600 |  | 250 | [6 empty] | 65 | 65 kA @ circuit breaker DIVQ/7 250A, 480Vac | 65 kA @ circuit breaker DIVQ/7 250A, 480Vac | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/33150.html | www.woehner.com/en/products/33150.html
32976 | Sammelschienenadapter 160 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 160 A, 3-pole, aligned to switchgear | 05 | 36 | 60250.1-L | 600 |  | 250 | [6 empty] | 65 | 65 kA @ circuit breaker DIVQ/7 250A, 480Vac | 25kA @ circuit breaker DIVQ/7 250A, 600Vac | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/33151.html | www.woehner.com/en/products/33151.html
32977 | Sammelschienenadapter 250 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 250 A, 3-pole, aligned to switchgear | 05 | 36 | 60250.1-L | 600 |  | 250 | [6 empty] | 200 | 200kA @ 3VL3 / 240V | 200kA @ 3VL3 / 240V | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/33160.html | www.woehner.com/en/products/33160.html
32978 | Sammelschienenadapter 630 A, 3-polig, angepasst auf Schaltgeräte | busbar adapter 630 A, 3-pole, aligned to switchgear | 05 | 42 | EPC60630-L | 600 |  | 630 |  |  |  |  | 30 |  |  |  |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/33161.html | www.woehner.com/en/products/33161.html
32981 | Sammelschienenadapter 100 A, angepasst auf Schaltgeräte | busbar adapter 100 A, aligned to switchgear | 05 | 28 | EEC60100-L | 600 |  | 100 | [8 empty] | 65kA @ circuit breakerSiemens S3 | Yes |  | UL listed | E123577 | NMTR | NMTR7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/33162.html | www.woehner.com/en/products/33162.html
33027 | Lasttrennschalter 3-polig 125 A | switch-disconnector 3-pole 125 A | 14 | 02 | SD3-3-125 | 600 |  | 125 | [6 empty] | 10 | 10 kA @ 600 V with RK5 max. 175 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/33198.html | www.woehner.com/en/products/33198.html
33028 | Lasttrennschalter 3-polig + N 125 A | switch-disconnector 3-pole + N 125 A | 14 | 02 | SD3-4-125 | 600 |  | 125 | [6 empty] | 10 | 10 kA @ 600 V with RK5 max. 175 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/33199.html | www.woehner.com/en/products/33199.html
33031 | Lasttrennschalter 3-polig 160 A | switch-disconnector 3-pole 160 A | 14 | 02 | SD3-3-160 | 600 |  | 160 | [6 empty] | 10 | 10 kA @ 600 V with RK5 max. 175 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/33200.html | www.woehner.com/en/products/33200.html
33032 | Lasttrennschalter 3-polig + N 160 A | switch-disconnector 3-pole + N 160 A | 14 | 02 | SD3-4-160 | 600 |  | 160 | [6 empty] | 10 | 10 kA @ 600 V with RK5 max. 175 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/33201.html | www.woehner.com/en/products/33201.html
33037 | Lasttrennschalter 3-polig + N 125 A | switch-disconnector 3-pole + N 125 A | 14 | 02 | SD3-4-125 | 600 |  | 125 | [6 empty] | 10 | 10 kA @ 600 V with RK5 max. 175 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/33202.html | www.woehner.com/en/products/33202.html
33041 | Lasttrennschalter 3-polig + N 160 A | switch-disconnector 3-pole + N 160 A | 14 | 02 | SD3-4-160 | 600 |  | 160 | [6 empty] | 10 | 10 kA @ 600 V with RK5 max. 175 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/33203.html | www.woehner.com/en/products/33203.html
33075 | NH-Sicherungs-Lasttrennschalter Gr. 00, 160 A, Reiter, Anschluss unten / oben | NH fuse-switch-disconnector size 00, 160 A, busbar mounted, connection top / bottom | 09 | 24 | QCB-NH00 | 600 |  | 160 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33206.html | www.woehner.com/en/products/33206.html
33079 | NH-Sicherungs-Lasttrennschalter Gr. 00, 160 A, Reiter, Anschluss unten / oben | NH fuse-switch-disconnector size 00, 160 A, busbar mounted, connection top / bottom | 09 | 24 | QCB-NH00 | 600 |  | 160 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33207.html | www.woehner.com/en/products/33207.html
33149 | NH-Sicherungs-Lasttrennschalter Gr. 1, 250 A, Aufbau | NH fuse switch-discon. size 1, 250 A, panel mounting | 09 | 07 | QCB-NH1 | 600 |  | 250 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33208.html | www.woehner.com/en/products/33208.html
33150 | NH-Sicherungs-Lasttrennschalter Gr. 2, 400 A, Aufbau | NH fuse switch-discon. size 2, 400 A, panel mounting | 09 | 10 | LTS-2 | 600 |  | 400 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33216.html | www.woehner.com/en/products/33216.html
33151 | NH-Sicherungs-Lasttrennschalter Gr. 3, 630 A, Aufbau | NH fuse switch-discon. size 3, 630 A, panel mounting | 09 | 13 | LTS-3 | 600 |  | 600 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33217.html | www.woehner.com/en/products/33217.html
33160 | NH-Sicherungs-Lasttrennschalter Gr. 1, 250 A, Reiter, Anschluss unten / oben | NH fuse switch-disconnector size 1, 250 A, busbar mounted, connection top / bottom | 09 | 28 | QCB-NH1 | 600 |  | 250 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33221.html | www.woehner.com/en/products/33221.html
33161 | NH-Sicherungs-Lasttrennschalter Gr. 2, 400 A, Reiter, Anschluss unten / oben | NH fuse switch-disconnector size 2, 400 A, busbar mounted, connection top / bottom | 09 | 31 | LTS-2 | 600 |  | 400 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33222.html | www.woehner.com/en/products/33222.html
33162 | NH-Sicherungs-Lasttrennschalter Gr. 3, 630 A, Reiter, Anschluss unten / oben | NH fuse switch-disconnector size 3, 630 A, busbar mounted, connection top / bottom | 09 | 34 | LTS-3 | 600 |  | 600 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33306.html | www.woehner.com/en/products/33306.html
33198 | NH-Sicherungs-Lasttrennschalter Gr. 00, 160 A, Reiter, Anschluss unten / oben | NH fuse switch-disconnector size 00, 160 A, busbar mounted, connection top / bottom | 09 | 24 | QCB-NH00 | 600 |  | 160 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33307.html | www.woehner.com/en/products/33307.html
33199 | NH-Sicherungs-Lasttrennschalter Gr. 00, 160 A, Aufbau | NH fuse switch-disconnector size 00, 160 A, panel mounting | 09 | 03 | LTS-00 | 600 |  | 160 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33308.html | www.woehner.com/en/products/33308.html
33200 | NH-Sicherungs-Lasttrennschalter Gr. 00, 160 A, Aufbau | NH fuse switch-disconnector size 00, 160 A, panel mounting | 09 | 03 | LTS-00 | 600 |  | 160 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33309.html | www.woehner.com/en/products/33309.html
33201 | NH-Sicherungs-Lasttrennschalter Gr. 1, 250 A, Aufbau | NH fuse switch-discon. size 1, 250 A, panel mounting | 09 | 06 | QCB-NH1 | 600 |  | 250 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33310.html | www.woehner.com/en/products/33310.html
33202 | NH-Sicherungs-Lasttrennschalter Gr. 2, 400 A, Aufbau | NH fuse switch-discon. size 2, 400 A, panel mounting | 09 | 09 | LTS-2 | 600 |  | 400 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33311.html | www.woehner.com/en/products/33311.html
33203 | NH-Sicherungs-Lasttrennschalter Gr. 3, 630 A, Aufbau | NH fuse switch-discon. size 3, 630 A, panel mounting | 09 | 12 | LTS-3 | 600 |  | 600 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33324.html | www.woehner.com/en/products/33324.html
33206 | NH-Sicherungs-Lasttrennschalter Gr. 00, 160 A, Reiter, Anschluss unten / oben | NH fuse switch-disconnector size 00, 160 A, busbar mounted, connection top / bottom | 09 | 25 | QCB-NH00 | 600 |  | 160 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33325.html | www.woehner.com/en/products/33325.html
33207 | NH-Sicherungs-Lasttrennschalter Gr. 00, 160 A, Aufbau | NH fuse switch-disconnector size 00, 160 A, panel mounting | 09 | 04 | LTS-00 | 600 |  | 160 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33326.html | www.woehner.com/en/products/33326.html
33208 | NH-Sicherungs-Lasttrennschalter Gr. 00, 160 A, Aufbau | NH fuse switch-disconnector size 00, 160 A, panel mounting | 09 | 04 | LTS-00 | 600 |  | 160 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33327.html | www.woehner.com/en/products/33327.html
33216 | NH-Sicherungs-Lasttrennschalter Gr. 000, 125 A, Reiter, Anschluss unten / oben | NH fuse switch-disconnector size 000, 125 A, busbar mounted, connection top / bottom | 09 | 22 | LTS-000 | 600 |  | 125 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33328.html | www.woehner.com/en/products/33328.html
33217 | NH-Sicherungs-Lasttrennschalter Gr. 000, 125 A, Aufbau | NH fuse switch-disconnector size 000, 125 A, panel mounting | 09 | 01 | LTS-000 | 600 |  | 125 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33329.html | www.woehner.com/en/products/33329.html
33221 | NH-Sicherungs-Lasttrennschalter Gr. 00, 160 A, Aufbau | NH fuse switch-disconnector size 00, 160 A, panel mounting | 09 | 03 | LTS-00 | 600 |  | 160 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33330.html | www.woehner.com/en/products/33330.html
33222 | NH-Sicherungs-Lasttrennschalter Gr. 00, 160 A, Aufbau | NH fuse switch-disconnector size 00, 160 A, panel mounting | 09 | 03 | LTS-00 | 600 |  | 160 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33331.html | www.woehner.com/en/products/33331.html
33306 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 16 | 09 | JC100 | 600 | 600 | 100 |  |  |  | 200 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/33332.html | www.woehner.com/en/products/33332.html
33307 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 16 | 12 | JC200 | 600 | 600 | 200 |  |  |  | 200 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/33393.html | www.woehner.com/en/products/33393.html
33308 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 16 | 15 | JC400 | 600 | 600 | 400 |  |  |  | 200 | [5 empty] | Yes | Yes | UL listed | E230163 | IZLT | IZLT7 |  |  |  | 110285 | 3211-37 | www.woehner.com/de/products/33394.html | www.woehner.com/en/products/33394.html
33310 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 16 | 30 | JC200B | 600 | 600 | 200 |  |  |  | 65 | [5 empty] | Yes | Yes | UL recognized | E230163 | IZLT2 | IZLT8 | E123577 | NMTR | NMTR7 | 110285 | 3211-37 | www.woehner.com/de/products/33398.html | www.woehner.com/en/products/33398.html
33311 | Reiter-Sicherungshalter Class J, Anschluss unten oder oben | bus mounted fuse holder Class J, connection top / bottom | 16 | 33 | JC400B | 600 | 600 | 400 |  |  |  | 65 | [5 empty] | Yes | Yes | UL recognized | E230163 | IZLT2 | IZLT8 | E123577 | NMTR | NMTR7 | 110285 | 3211-37 | www.woehner.com/de/products/33402.html | www.woehner.com/en/products/33402.html
33324 | NH-Sicherungs-Lasttrennschalter Gr. 00, 160 A, Reiter, Anschluss unten / oben | NH fuse switch-disconnector size 00, 160 A, busbar mounted, connection top / bottom | 09 | 25 | QCB-NH00 | 600 |  | 160 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33403.html | www.woehner.com/en/products/33403.html
33325 | NH-Sicherungs-Lasttrennschalter Gr. 1, 250 A, Reiter, Anschluss unten / oben | NH fuse switch-disconnector size 1, 250 A, busbar mounted, connection top / bottom | 09 | 28 | QCB-NH1 | 600 |  | 250 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33408.html | www.woehner.com/en/products/33408.html
33326 | NH-Sicherungs-Lasttrennschalter Gr. 2, 400 A, Reiter, Anschluss unten / oben | NH fuse switch-disconnector size 2, 400 A, busbar mounted, connection top / bottom | 09 | 31 | LTS-2 | 600 |  | 400 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33409.html | www.woehner.com/en/products/33409.html
33327 | NH-Sicherungs-Lasttrennschalter Gr. 3, 630 A, Reiter, Anschluss unten / oben | NH fuse switch-disconnector size 3, 630 A, busbar mounted, connection top / bottom | 09 | 34 | LTS-3 | 600 |  | 600 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33416.html | www.woehner.com/en/products/33416.html
33328 | NH-Sicherungs-Lasttrennschalter Gr. 00, 160 A, Aufbau | NH fuse switch-disconnector size 00, 160 A, panel mounting | 09 | 04 | LTS-00 | 600 |  | 160 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33420.html | www.woehner.com/en/products/33420.html
33329 | NH-Sicherungs-Lasttrennschalter Gr. 00, 160 A, Aufbau | NH fuse switch-disconnector size 00, 160 A, panel mounting | 09 | 04 | LTS-00 | 600 |  | 160 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33421.html | www.woehner.com/en/products/33421.html
33330 | NH-Sicherungs-Lasttrennschalter Gr. 1, 250 A, Aufbau | NH fuse switch-discon. size 1, 250 A, panel mounting | 09 | 07 | QCB-NH1 | 600 |  | 250 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33422.html | www.woehner.com/en/products/33422.html
33331 | NH-Sicherungs-Lasttrennschalter Gr. 2, 400 A, Aufbau | NH fuse switch-discon. size 2, 400 A, panel mounting | 09 | 10 | LTS-2 | 600 |  | 400 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33600.html | www.woehner.com/en/products/33600.html
33332 | NH-Sicherungs-Lasttrennschalter Gr. 3, 630 A, Aufbau | NH fuse switch-discon. size 3, 630 A, panel mounting | 09 | 13 | LTS-3 | 600 |  | 600 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33601.html | www.woehner.com/en/products/33601.html
33393 | NH-Sicherungs-Lasttrennschalter Gr. 1, 250 A, Aufbau | NH fuse switch-discon. size 1, 250 A, panel mounting | 09 | 06 | QCB-NH1 | 600 |  | 250 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33602.html | www.woehner.com/en/products/33602.html
33394 | NH-Sicherungs-Lasttrennschalter Gr. 00, 160 A, Reiter, Anschluss unten / oben | NH fuse switch-disconnector size 00, 160 A, busbar mounted, connection top / bottom | 09 | 25 | QCB-NH00 | 600 |  | 160 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/33603.html | www.woehner.com/en/products/33603.html
33398 | NH-Sicherungs-Lasttrennschalter Gr. 00, 160 A, Reiter, Anschluss unten / oben | NH fuse switch-disconnector size 00, 160 A, busbar mounted, connection top / bottom | 09 | 24 | QCB-NH00 | 600 |  | 160 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/35001.html | www.woehner.com/en/products/35001.html
33402 | Reiter-Sicherungshalter Class J, Anschluss unten oder oben | busbar mounted fuse holder Class J, connection top / bottom | 16 | 27 | QCC-ClassJ100A | 600 | 600 | 100 |  |  |  | 200 | [5 empty] | Yes | Yes | UL recognized | E230163 | IZLT2 | IZLT8 | E123577 | NMTR | NMTR7 |  |  | www.woehner.com/de/products/35004.html | www.woehner.com/en/products/35004.html
33403 | Reiter-Sicherungshalter Class J, Anschluss unten oder oben | busbar mounted fuse holder Class J, connection top / bottom | 16 | 30 | QCC-ClassJ200A | 600 | 600 | 200 |  |  |  | 200 | [5 empty] | Yes | Yes | UL recognized | E230163 | IZLT2 | IZLT8 | E123577 | NMTR | NMTR7 |  |  | www.woehner.com/de/products/35005.html | www.woehner.com/en/products/35005.html
33408 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 16 | 09 | QCC-ClassJ100A | 600 | 600 | 100 |  |  |  | 200 | [5 empty] | Yes | Yes | UL recognized | E230163 | IZLT2 | IZLT8 | [5 empty] | www.woehner.com/de/products/35006.html | www.woehner.com/en/products/35006.html
33409 | Halter für zylindrische Sicherungen | holder for cylindrical fuses | 16 | 12 | QCC-ClassJ200A | 600 | 600 | 200 |  |  |  | 200 | [5 empty] | Yes | Yes | UL recognized | E230163 | IZLT2 | IZLT8 | [5 empty] | www.woehner.com/de/products/35007.html | www.woehner.com/en/products/35007.html
33416 | NH-Sicherungs-Lasttrennschalter Gr. 000, 125 A, Reiter, Anschluss unten / oben | NH fuse-switch-disconnector size 000, 125 A, busbar mounted, connection top / bottom | 09 | 22 | QCB-NH000 | 600 |  | 125 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/35008.html | www.woehner.com/en/products/35008.html
33420 | NH-Sicherungs-Lasttrennschalter Gr. 00, 160 A, Reiter, Anschluss unten / oben | NH fuse switch-disconnector size 00, 160 A, busbar mounted, connection top / bottom | 09 | 25 | QCB-NH00 | 600 |  | 160 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/35009.html | www.woehner.com/en/products/35009.html
33421 | Reiter-Sicherungshalter Class J, Anschluss oben oder unten | busbar mounted fuse holder Class J, connection top / bottom | 16 | 21 | QCC-ClassJ30A | 600 | 600 | 30 |  |  |  | 200 | [5 empty] | Yes | Yes | UL recognized | E230163 | IZLT2 | IZLT8 | E123577 | NMTR | NMTR7 |  |  | www.woehner.com/de/products/35015.html | www.woehner.com/en/products/35015.html
33422 | Reiter-Sicherungshalter Class J, Anschluss oben oder unten | busbar mounted fuse holder Class J, connection top / bottom | 16 | 24 | QCC-ClassJ60A | 600 | 600 | 60 |  |  |  | 200 | [5 empty] | Yes | Yes | UL recognized | E230163 | IZLT2 | IZLT8 | E123577 | NMTR | NMTR7 |  |  | www.woehner.com/de/products/35016.html | www.woehner.com/en/products/35016.html
33600 | NH-Sicherungs-Lasttrennschalter Gr. 1, 250 A, Reiter, Anschluss unten / oben | NH fuse switch-disconnector size 1, 250 A, busbar mounted, connection top / bottom | 09 | 27 | QCB-NH1 | 600 |  | 250 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/36001.html | www.woehner.com/en/products/36001.html
33601 | NH-Sicherungs-Lasttrennschalter Gr. 1, 250 A, Reiter, Anschluss unten / oben | NH fuse switch-disconnector size 1, 250 A, busbar mounted, connection top / bottom | 09 | 27 | QCB-NH1 | 600 |  | 250 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/36003.html | www.woehner.com/en/products/36003.html
33602 | NH-Sicherungs-Lasttrennschalter Gr. 2, 400 A, Reiter, Anschluss unten / oben | NH fuse switch-disconnector size 2, 400 A, busbar mounted, connection top / bottom | 09 | 30 | LTS-2 | 600 |  | 400 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/36009.html | www.woehner.com/en/products/36009.html
33603 | NH-Sicherungs-Lasttrennschalter Gr. 3, 630 A, Reiter, Anschluss unten / oben | NH fuse switch-disconnector size 3, 630 A, busbar mounted, connection top / bottom | 09 | 33 | LTS-3 | 600 |  | 600 |  |  |  | 100 | [5 empty] | Yes |  | UL recognized | E230163 | IZLT2 | [6 empty] | www.woehner.com/de/products/36100.html | www.woehner.com/en/products/36100.html
33808 | Lasttrennschalter 3-polig 16 A | switch-disconnector 3-pole 16 A | 14 | 01 | SD1-3-16 | 600 |  | 16 | [6 empty] | 5 | 5 kA @ 600 V with RK5 max. 40 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/36101.html | www.woehner.com/en/products/36101.html
33809 | Lasttrennschalter 3-polig + N 16 A | switch-disconnector 3-pole + N 16 A | 14 | 01 | SD1-4-16 | 600 |  | 16 | [6 empty] | 5 | 5 kA @ 600 V with RK5 max. 40 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/36102.html | www.woehner.com/en/products/36102.html
33812 | Lasttrennschalter 3-polig 25 A | switch-disconnector 3-pole 25 A | 14 | 01 | SD1-3-25 | 600 |  | 25 | [6 empty] | 5 | 5 kA @ 600 V with RK5 max. 40 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/36103.html | www.woehner.com/en/products/36103.html
33813 | Lasttrennschalter 3-polig + N 25 A | switch-disconnector 3-pole + N 25 A | 14 | 01 | SD1-4-25 | 600 |  | 25 | [6 empty] | 5 | 5 kA @ 600 V with RK5 max. 40 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/36104.html | www.woehner.com/en/products/36104.html
33816 | Lasttrennschalter 3-polig 32 A | switch-disconnector 3-pole 32 A | 14 | 01 | SD1-3-32 | 600 |  | 32 | [6 empty] | 5 | 5 kA @ 600 V with RK5 max. 40 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/36105.html | www.woehner.com/en/products/36105.html
33817 | Lasttrennschalter 3-polig + N 32 A | switch-disconnector 3-pole + N 32 A | 14 | 01 | SD1-4-32 | 600 |  | 32 | [6 empty] | 5 | 5 kA @ 600 V with RK5 max. 40 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/36106.html | www.woehner.com/en/products/36106.html
33820 | Lasttrennschalter 3-polig 40 A | switch-disconnector 3-pole 40 A | 14 | 01 | SD1-3-40 | 600 |  | 40 | [6 empty] | 5 | 5 kA @ 600 V with RK5 max. 40 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/36107.html | www.woehner.com/en/products/36107.html
33839 | Lasttrennschalter 3-polig + N 16 A | switch-disconnector 3-pole + N 16 A | 14 | 01 | SD1-4-16 | 600 |  | 16 | [6 empty] | 5 | 5 kA @ 600 V with RK5 max. 40 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/36108.html | www.woehner.com/en/products/36108.html
33843 | Lasttrennschalter 3-polig + N 25 A | switch-disconnector 3-pole + N 25 A | 14 | 01 | SD1-4-25 | 600 |  | 25 | [6 empty] | 5 | 5 kA @ 600 V with RK5 max. 40 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/36109.html | www.woehner.com/en/products/36109.html
33847 | Lasttrennschalter 3-polig + N 32 A | switch-disconnector 3-pole + N 25 A | 14 | 01 | SD1-4-32 | 600 |  | 32 | [6 empty] | 5 | 5 kA @ 600 V with RK5 max. 40 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/36110.html | www.woehner.com/en/products/36110.html
33851 | Lasttrennschalter 3-polig + N 40 A | switch-disconnector 3-pole + N 40 A | 14 | 01 | SD1-4-40 | 600 |  | 40 | [6 empty] | 5 | 5 kA @ 600 V with RK5 max. 40 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/36111.html | www.woehner.com/en/products/36111.html
33868 | Lasttrennschalter 3-polig 63 A | switch-disconnector 3-pole 63 A | 14 | 01 | SD2-3-63 | 600 |  | 63 | [6 empty] | 5 | 5 kA @ 600 V with RK5 max. 80 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/36112.html | www.woehner.com/en/products/36112.html
33869 | Lasttrennschalter 3-polig + N 63 A | switch-disconnector 3-pole + N 63 A | 14 | 01 | SD2-4-63 | 600 |  | 63 | [6 empty] | 5 | 5 kA @ 600 V with RK5 max. 80 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/36113.html | www.woehner.com/en/products/36113.html
33872 | Lasttrennschalter 3-polig 80 A | switch-disconnector 3-pole 80 A | 14 | 01 | SD2-3-80 | 600 |  | 80 | [6 empty] | 5 | 5 kA @ 600 V with RK5 max. 80 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/36114.html | www.woehner.com/en/products/36114.html
33873 | Lasttrennschalter 3-polig + N 80 A | switch-disconnector 3-pole + N 80 A | 14 | 01 | SD2-4-80 | 600 |  | 80 | [6 empty] | 5 | 5 kA @ 600 V with RK5 max. 80 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/36155.html | www.woehner.com/en/products/36155.html
33876 | Lasttrennschalter 3-polig 100 A | switch-disconnector 3-pole 100 A | 14 | 02 | SD2-3-100 | 600 |  | 100 | [6 empty] | 5 | 5 kA @ 600 V with RK5 max. 80 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/36156.html | www.woehner.com/en/products/36156.html
33877 | Lasttrennschalter 3-polig + N 100 A | switch-disconnector 3-pole + N 100 A | 14 | 02 | SD2-4-100 | 600 |  | 100 | [6 empty] | 5 | 5 kA @ 600 V with RK5 max. 80 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/36157.html | www.woehner.com/en/products/36157.html
33885 | Lasttrennschalter 3-polig + N 63 A | switch-disconnector 3-pole + N 63 A | 14 | 01 | SD2-4-63 | 600 |  | 63 | [6 empty] | 5 | 5 kA @ 600 V with RK5 max. 80 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/36158.html | www.woehner.com/en/products/36158.html
33889 | Lasttrennschalter 3-polig + N 80 A | switch-disconnector 3-pole + N 80 A | 14 | 01 | SD2-4-80 | 600 |  | 80 | [6 empty] | 5 | 5 kA @ 600 V with RK5 max. 80 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/36159.html | www.woehner.com/en/products/36159.html
33893 | Lasttrennschalter 3-polig + N 100 A | switch-disconnector 3-pole + N 100 A | 14 | 02 | SD2-4-100 | 600 |  | 100 | [6 empty] | 5 | 5 kA @ 600 V with RK5 max. 80 A |  |  |  | UL listed | E506215 | NLRV | NLRV7 | [5 empty] | www.woehner.com/de/products/36200.html | www.woehner.com/en/products/36200.html
35001 | Schienenträger, 3-polig, mittig | busbar support, 3-pole, centre | 11 | 15 | Z1140-L | 600 | [11 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/36209.html | www.woehner.com/en/products/36209.html
35004 | Zentraleinspeisung 2000 A | centre feed unit 2000 A | 11 | 12 | CentreFeedUnit | 600 |  | 1400 | [6 empty] | 103 | fuse Class L 1600 A / 600 V AC |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/36215.html | www.woehner.com/en/products/36215.html
35005 | Zentraleinspeisung 2000 A | centre feed unit 2000 A | 11 | 12 | CentreFeedUnit | 600 |  | 1400 | [6 empty] | 103 | fuse Class L 1600 A / 600 V AC |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/36216.html | www.woehner.com/en/products/36216.html
35006 | Zentraleinspeisung 1250 A | centre feed unit 1250 A | 11 | 12 | CentreFeedUnit | 480 |  | 1200 | [6 empty] | 45 | circuit breaker DIVQ 1200 / 480 V AC |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/36218.html | www.woehner.com/en/products/36218.html
35007 | Zentraleinspeisung 1250 A | centre feed unit 1250 A | 11 | 12 | CentreFeedUnit | 480 |  | 1200 | [6 empty] | 45 | circuit breaker DIVQ 1200 / 480 V AC |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/36219.html | www.woehner.com/en/products/36219.html
35008 | Schienenträger, außen | busbar support, lateral | 11 | 15 | Z1140-L | 600 | [11 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/36220.html | www.woehner.com/en/products/36220.html
35009 | Schienenträger, 4-polig, mittig | busbar support, 4-pole, centre | 11 | 15 | Z1140-L | 600 | [11 empty] | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/36905.html | www.woehner.com/en/products/36905.html
35015 | Zentraleinspeisung 3200 A | centre feed unit 3200 A | 11 | 12 | CentreFeedUnit | 600 |  | 1800 | [6 empty] | 103 | fuse Class L 1600 A / 600 V AC |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/36906.html | www.woehner.com/en/products/36906.html
35016 | Zentraleinspeisung 3200 A | centre feed unit 3200 A | 11 | 12 | CentreFeedUnit | 600 |  | 1800 | [6 empty] | 103 | fuse Class L 1600 A / 600 V AC |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/36907.html | www.woehner.com/en/products/36907.html
36001 | Sammelschienenadapter 16 A, mit CrossLink®Technology | busbar adapter 16 A, with CrossLink®Technology | 05 | 21 | EQ22-A | 600 |  | 12,5 |  |  |  |  | 6 | 3 cycles (without OPD) @ 600 V AC | 50 | fuse JDDZ Class CC 20 A @ 600 V AC |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/36908.html | www.woehner.com/en/products/36908.html
36003 | Sammelschienenadapter 16 A, mit CrossLink®Technology | busbar adapter 16 A, with CrossLink®Technology | 05 | 21 | EQ22-A | 600 |  | 12,5 |  |  |  |  | 6 | 3 cycles (without OPD) @ 600 V AC | 50 | fuse JDDZ Class CC 20 A @ 600 V AC |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/36911.html | www.woehner.com/en/products/36911.html
36009 | Adapter 16 A, mit CrossLink®-Schnittstelle | Adapter 16A, with CrossLink® interface | 05 | 21 | EQ22-A1 | 600 |  | 12,5 |  |  |  |  | 6 | 3 cycles (without OPD) @ 600 V AC | 50 | fuse JDDZ Class CC 20 A @ 600 V AC |  | Yes |  | UL listed | E123577 | NMTR | NMTR7 | [5 empty] | www.woehner.com/de/products/36912.html | www.woehner.com/en/products/36912.html
36100 | Hybrid-Motorstarter | hybrid motor starter | 21 | 03 | MCC 36100 | 500 |  | 0,6 | [9 empty] | Yes |  | UL listed | E360470 | NLDX | NLDX7 | [5 empty] | www.woehner.com/de/products/36913.html | www.woehner.com/en/products/36913.html
36101 | Hybrid-Motorstarter | hybrid motor starter | 21 | 06 | MCC 36101 | 500 |  | 0,6 | [9 empty] | Yes |  | UL listed | E360470 | NLDX | NLDX7
36102 | Hybrid-Motorstarter | hybrid motor starter | 21 | 09 | MCC 36102 | 500 |  | 0,6 | [9 empty] | Yes |  | UL listed | E360470 | NLDX | NLDX7
36103 | Hybrid-Motorstarter | hybrid motor starter | 21 | 03 | MCC 36103 | 500 |  | 2 | [9 empty] | Yes |  | UL listed | E360470 | NLDX | NLDX7
36104 | Hybrid-Motorstarter | hybrid motor starter | 21 | 06 | MCC 36104 | 500 |  | 2 | [9 empty] | Yes |  | UL listed | E360470 | NLDX | NLDX7
36105 | Hybrid-Motorstarter | hybrid motor starter | 21 | 09 | MCC 36105 | 500 |  | 2 | [9 empty] | Yes |  | UL listed | E360470 | NLDX | NLDX7
36106 | Hybrid-Motorstarter | hybrid motor starter | 21 | 03 | MCC 36106 | 500 |  | 6,5 | [9 empty] | Yes |  | UL listed | E360470 | NLDX | NLDX7
36107 | Hybrid-Motorstarter | hybrid motor starter | 21 | 06 | MCC 36107 | 500 |  | 6,5 | [9 empty] | Yes |  | UL listed | E360470 | NLDX | NLDX7
36108 | Hybrid-Motorstarter | hybrid motor starter | 21 | 09 | MCC 36108 | 500 |  | 6,5 | [9 empty] | Yes |  | UL listed | E360470 | NLDX | NLDX7
36109 | Hybrid-Motorstarter, 3-polig | hybrid motor starter, 3-pole | 21 | 51 | 36109 | 500 |  | 0,6 | [9 empty] | Yes |  | UL listed | E360470 | NLDX | NLDX7
36110 | Hybrid-Motorstarter, 3-polig | hybrid motor starter, 3-pole | 21 | 51 | 36110 | 500 |  | 2 | [9 empty] | Yes |  | UL listed | E360470 | NLDX | NLDX7
36111 | Hybrid-Motorstarter, 3-polig | hybrid motor starter, 3-pole | 21 | 51 | 36111 | 500 |  | 6,5 | [9 empty] | Yes |  | UL listed | E360470 | NLDX | NLDX7
36112 | Ersatzteil für MOTUS®Panel | spare part for MOTUS®Panel | 05 | 58 | MCC-PA | 600 |  | 20 |  |  |  |  | 6 | 3 cycles (without OPD) @ 600 V AC | 50 | fuse JDDZ Class CC 20 A @ 600 V AC |  | Yes |  | UL listed | E360470 | NLDX | NLDX7
36113 | Ersatzteil Sammelschienenadapter 25 A | spare part busbar adapter 25 A | 05 | 58 | MCC-30 | 600 |  | 12,5 |  |  |  |  | 6 | 3 cycles (without OPD) @ 600 V AC | 50 | fuse JDDZ Class CC 20 A @ 600 V AC |  | Yes |  | UL listed | E360470 | NLDX | NLDX7
36114 | Ersatzteil Sammelschienenadapter 25 A | spare part busbar adapter 25 A | 05 | 58 | MCC-60 | 600 |  | 12,5 |  |  |  |  | 6 | 3 cycles (without OPD) @ 600 V AC | 50 | fuse JDDZ Class CC 20 A @ 600 V AC |  | Yes |  | UL listed | E360470 | NLDX | NLDX7
36155 | Ersatzteil Sammelschienenadapter 25 A | spare part busbar adapter 25 A | 05 | 58 |  | 500 | [11 empty] | Yes |  | UL listed | E483362 | NRNT | NRNT7
36156 | Ersatzteil Sammelschienenadapter 25 A | spare part busbar adapter 25 A | 05 | 58 |  | 500 | [11 empty] | Yes |  | UL listed | E483362 | NRNT | NRNT7
36157 | Hybridschalter, 3- oder 1-polig schaltbar | hybrid switch, 3-pole or 1-pole switchable | 21 | 15 | OM25-H-30 | 480 |  | 20 | [6 empty] | 30 | fuse JDDZ Class CC 30 A @ 480 V AC |  | Yes |  | UL listed | E483362 | NRNT | NRNT7
36158 | Hybridschalter, 3- oder 1-polig schaltbar | hybrid switch, 3-pole or 1-pole switchable | 21 | 18 | OM25-H-60 | 480 |  | 20 | [6 empty] | 30 | fuse JDDZ Class CC 30 A @ 480 V AC |  | Yes |  | UL listed | E483362 | NRNT | NRNT7
36159 | Hybridschalter, 3- oder 1-polig schaltbar | hybrid switch, 3-pole or 1-pole switchable | 21 | 51 | OM25-H | 480 |  | 20 | [6 empty] | 30 | fuse JDDZ Class CC 30 A @ 480 V AC |  | Yes |  | UL listed | E483362 | NRNT | NRNT7
36200 | Netzteil 400 V AC / 24 V DC, 10 A | power supply 400 V AC / 24 V DC, 10 A | 21 | 40 | BROOME 10 | 480 | [11 empty] | Yes |  | UL listed | E497002 | NMTR_ | NMTR7.
36209 | Busmodul SmartWireDT | bus module SmartWireDT | 21 | 24 | SWD 36209 | [14 empty] | UL listed | E360470 | NLDX | NLDX7
36215 | Powerfeed 24 V für SmartWire-DT | power feed 24V for SmartWire-DT | 21 | 56 | EU5C-SWD-PF2-1 | [14 empty] | UL listed | E29184 | NKCR |  |  |  |  | 012528 | 3211-07
36216 | Gateway Profibus DP zu SmartWire-DT | gateway Profibus DP to SmartWire-DT | 21 | 21 | EU5C-SWD-DP | [14 empty] | UL listed | E29184 | NKCR |  |  |  |  | 012528 | 3211-07
36218 | Gateway CANopen zu SmartWire-DT | gateway CANopen to SmartWire-DT | 21 | 21 | EU5C-SWD-CAN | [14 empty] | UL listed | E29184 | NKCR |  |  |  |  | 012528 | 3211-07
36219 | Gateway EtherNet/IP zu SmartWire-DT | gateway EtherNet/IP to SmartWire-DT | 21 | 21 | EU5C-SWD-EIP-MODTCP | [14 empty] | UL listed | E29184 | NKCR |  |  |  |  | 012528 | 3211-07
36220 | Gateway Profinet zu SmartWire-DT | gateway Profinet to SmartWire-DT | 21 | 21 | [15 empty] | UL listed | E29184 | NKCR |  |  |  |  | 012528 | 3211-07
36905 | Flachbandleitung 8-polig | ribbon cable 8-pole | 21 | 56 | SWD4-3LF8-24-2S | [14 empty] | UL listed | E29184 | NKCR |  |  |  |  | 012528 | 3211-07
36906 | Gerätestecker | device plug | 21 | 56 | SWD4-8SF2-5 | [14 empty] | UL listed | E29184 | NKCR |  |  |  |  | 012528 | 3211-07
36907 | Flachstecker Gateway und Powerfeed | flat plug gateway and power feed | 21 | 56 | SWD4-8MF2 | [14 empty] | UL listed | E29184 | NKCR |  |  |  |  | 012528 | 3211-07
36908 | Netzwerkabschluss | network termination | 21 | 56 | SWD4-RC8-10 | [14 empty] | UL listed | E29184 | NKCR |  |  |  |  | 012528 | 3211-07
36911 | USB-Kabel | USB cable | 21 | 56 | [15 empty] | UL listed | E29184 | NKCR |  |  |  |  | 012528 | 3211-07
36912 | Brücke | bridge | 21 | 56 | [15 empty] | UL listed | E29184 | NKCR |  |  |  |  | 012528 | 3211-07
36913 | Kupplung | coupling | 21 | 56 | [15 empty] | UL listed | E29184 | NKCR |  |  |  |  | 012528 | 3211-07